## Cover
Archive Files
Document Number: ZW-YF-JS-PVESS.T12-XY-0.1.1-1.0-201610
File name: MODBUS Communication Protocol
Version: V1.0
Department: R&D
Draft:
Audit:
approve:
Archive date:

## Protocol Description
1. ModBus communication protocol is divided into RTU protocol and ASCII protocol. Our company adopts RTU protocol.
2. Serial port configuration
| Start bit | 1st
| Data bits | 8-bit
| Parity bit | none
| Stop bits | 1st
3. The communication baud rate is 9600
4. Read data using 03 function code
5. Write data using 10 Function code
Data Request: | Address code | 1 byte | System Address
| Function code | 1 byte | 0 x03
| Starting address | 2 bytes | Register Address | 0x0000 to 0xFFFF
| Number of registers | 2 bytes | 1 -125
| CRC Check | 2 bytes | The lower 8 bits are in front, the higher 8 bits are in the back
Data reply: | Address code | 1 byte | System Address
| Function code | 1 byte | 0 x03
| Number of bytes | 1 byte | 2*N
| Register Value | 2*N bytes | 1 -125
| CRC Check | 2 bytes | The lower 8 bits are in front, the higher 8 bits are in the back
N: Number of requested registers
Error response: | Address code | 1 byte | System Address
| Function code | 1 byte | 0x03+0x80
| Exception code | 1 byte | 01, 02, 03 or 04
| CRC Check | 2 bytes | The lower 8 bits are in front, the higher 8 bits are in the back
Modify registers: | Address code | 1 byte | System Address
| Function code | 1 byte | 0x 10
| Starting address | 2 bytes | Register Address
| Number of registers | 2 bytes | 1-12 3
| Number of bytes | 1 byte
| Write value 2*N | 2*N bytes
| CRC Check | 2 bytes | The lower 8 bits are in front, the higher 8 bits are in the back
reply | Address code | 1 byte | System Address
| Function code | 1 byte | 0x 10
| Starting address | 2 bytes | Register Address
| Number of registers | 2 bytes | 1-12 3
| CRC Check | 2 bytes | The lower 8 bits are in front, the higher 8 bits are in the back
7. Interface Definition

## data
Inverter unit real-time data | [8 empty] | Data Types |  | Table 2-1 Operation mode |  | Table 1-1: Inverter status |  |  | Table 1-2 : Battery status
Order | Register Address | Data Type | What the data means | Number of bytes | R/W | unit |  | Remark |  |  | 0 | Standby |  | 1 | 0 |  | 1 | 0
0x03 | 0 | Status word 0 | Inverter state | 2 | R |  |  | Table 1-1 |  |  | 1 | DC voltage source | bit15 |  |  | bit15
0x03 | 1 | Status word 1 | Battery Status | 2 | R |  |  | Table 1-2 |  |  | 2 | AC voltage source | bit14 |  |  | bit14
0x03 | 2 | Status word 2 | Switch Status | 2 | R |  |  | Table 1-3 |  |  | 3 |  | bit13 |  |  | bit13
0x03 | 3 | Status word 3 | Photovoltaic status | 2 | R |  |  | Table 1-4 |  |  | 4 | Power Control | bit12 | Bus voltage out of range | For debugging | bit12 | Busbar overvoltage 2
0x03 | 4 | Status word 4 | Grid oil generator status | 2 | R |  |  | Table 1-5 |  |  | 5 |  | bit11 | Slow start, not completed | For debugging | bit11 | DC hardware overcurrent 1
0x03 | 5 | Status word 5 | Output Status | 2 | R |  |  | Table 1-6 |  |  | 6 | Time-based power control | bit10 | Bus voltage out of range | For debugging | bit10
0x03 | 6 | Parameter 0 | Working Mode | 2 | R/W |  |  | Table 2-1 |  |  | 7 | PQ Run | bit9 |  |  | bit9 | Bus undervoltage
0x03 | 7 | Parameter 1 |  | 2 | R/W | [5 empty] | 8 | Automatic on-grid and off-grid switching power control | bit8 |  |  | bit8 | Busbar overvoltage 1
0x03 | 8 | Parameter 2 | Photovoltaic mode | 2 | R/W | [5 empty] | 9 |  | bit7 | Self-test failed |  | bit7 | Battery switch voltage difference is normal
0x03 | 9 | Parameter 3 | Grid-connected power | 2 | R/W | [5 empty] | 10 | Automatic on-grid and off-grid switching, power control based on time | bit6 |  |  | bit6 | Low voltage DC overvoltage
0x03 | 10 | Parameter 4 |  | 2 | R/W | [7 empty] | bit5 | Phase lock abnormality |  | bit5
0x03 | 11 | Parameter 5 | DC bus reference voltage | 2 | R/W | [7 empty] | bit4 | Over temperature |  | bit4
0x03 | 12 | Parameter 6 | Battery reference voltage | 2 | R/W | [7 empty] | bit3 | AC hardware overcurrent |  | bit3 | DC hardware overcurrent
0x03 | 13 | Parameter 7 |  | 2 | R/W | [7 empty] | bit2 | AC software overcurrent |  | bit2
0x03 | 14 | Parameter 8 |  | 2 | R/W | [7 empty] | bit1 | Busbar overvoltage |  | bit1 | Battery overvoltage
0x03 | 15 | Parameter 9 | Power on/off command | 2 | R/W | [7 empty] | bit0 | Abnormal load voltage |  | bit0 | Battery low voltage
0x03 | 16 | Parameter 10 |  | 2 | R/W | [5 empty] | Table 2-2 Power on/off commands |  | Table 1-3 : Switch status |  |  | Table 1-4 ：Photovoltaic state
0x03 | 17 | Parameter 11 |  | 2 | R/W | [6 empty] | 1 |  | 1 | 0 |  | 1 | 0
0x03 | 18 | Command word 0 |  | 2 | R/W | [5 empty] | bit15 |  | bit15 | Grid relay closes and supplies power |  | bit15
0x03 | 19 | Command word 1 |  | 2 | R/W | [5 empty] | bit14 |  | bit14 | Inverter voltage source power supply |  | bit14
0x03 | 20 | Command word 2 | INV software BOOT version number | 2 | R/W | [5 empty] | bit13 |  | bit13 | Inverter current source power supply |  | bit13
0x03 | 21 | Command word 3 | INV software version low 8 digit minor version | 2 | R/W | [5 empty] | bit12 |  | bit12 |  |  | bit12
0x03 | 22 | Waveform channel 0 |  | 2 | R/W | [5 empty] | bit11 |  | bit11 | Oil engine relay closes and supplies power |  | bit11
0x03 | 23 | Waveform channel 1 |  | 2 | R/W | [5 empty] | bit10 |  | bit10 |  |  | bit10
0x03 | 24 | Waveform channel 2 |  | 2 | R/W | [5 empty] | bit9 | bit9-bit8: 1 bypass start 2 bypass shutdown | bit9 | smartload on |  | bit9
0x03 | 25 | Waveform channel 3 |  | 2 | R/W | [5 empty] | bit8 |  | bit8 | Switch on |  | bit8
0x03 | 26 | Data0 | Inverter voltage | 2 | R | 0.1 | V |  | UINT16 |  | bit7 |  | bit7 |  |  | bit7 | Photovoltaic 2 overvoltage
0x03 | 27 | Data 1 | Inverter current | 2 | R | 0.01 | A |  | UINT16 |  | bit6 |  | bit6 |  |  | bit6
0x03 | 28 | Data 2 | Load voltage | 2 | R | 0.1 | V |  | UINT16 |  | bit5 | bit5-bit4: 1 unbalanced power on 2 unbalanced power off | bit5 | DC normal operation |  | bit5
0x03 | 29 | Data 3 | Load current | 2 | R | 0.01 | A |  | UINT16 |  | bit4 |  | bit4 |  |  | bit4 | Photovoltaic 1 overvoltage
0x03 | 30 | Data 4 | Grid voltage | 2 | R | 0.1 | V |  | UINT16 |  | bit3 |  | bit3 |  |  | bit3 | Photovoltaic hardware overcurrent
0x03 | 31 | Data 5 | Grid current | 2 | R | 0.01 | A |  | UINT16 |  | bit2 |  | bit2 |  |  | bit2 | PV 2 undervoltage
0x03 | 32 | Data 6 | Oil engine voltage | 2 | R | 0.1 | V |  | UINT16 |  | bit1 | bit1-bit0: 1 inverter on 2 inverter off | bit1 | PV2 operation |  | bit1
0x03 | 33 | Data 7 | Oil engine current | 2 | R | 0.01 | A |  | UINT16 |  | bit0 |  | bit0 | PV1 operation |  | bit0 | PV 1 undervoltage
0x03 | 34 | Data 8 | Load voltage frequency | 2 | R | 0.01 | Hz |  | UINT16 |  |  |  | Table 1-5: Grid and diesel engine status |  |  | Table 1-6: Output state
0x03 | 35 | Data 9 | Grid voltage frequency | 2 | R | 0.01 | Hz |  | UINT16 |  |  |  |  | 1 | 0 |  | 1 | 0
0x03 | 36 | Data 10 | Engine voltage frequency | 2 | R | 0.01 | Hz |  | UINT16 |  |  |  | bit15 | Grid power supply | Power on | bit15
0x03 | 37 | Data 11 | Bus voltage | 2 | R | 0.1 | V |  | UINT16 |  |  |  | bit14 |  |  | bit14 | Communication logo | For debugging
0x03 | 38 | Data 12 | Photovoltaic 1 voltage | 2 | R | 0.1 | V |  | INT16 |  |  |  | bit13 | Anti-islanding frequency anomaly | For debugging | bit13 | Communication logo | For debugging
0x03 | 39 | Data 13 | Photovoltaic 1 current | 2 | R | 0.01 | A |  | INT16 |  |  |  | bit12 |  |  | bit12 | Communication logo | For debugging
0x03 | 40 | Data 14 | Photovoltaic 2 voltage | 2 | R | 0.1 | V |  | INT16 |  |  |  | bit11 |  |  | bit11 | Large difference 1 | For debugging
0x03 | 41 | Data 15 | Photovoltaic 2 current | 2 | R | 0.01 | A |  | INT16 |  |  |  | bit10 | Abnormal grid frequency |  | bit10 | Large difference | For debugging
0x03 | 42 | Data 16 | Battery voltage | 2 | R | 0.01 | V |  | INT16 |  |  |  | bit9 | Abnormal power grid amplitude |  | bit9 | Big difference | For debugging
0x03 | 43 | Data 17 | Battery Current | 2 | R | 0.1 | A | Positive means discharging, negative means charging | INT16 |  |  |  | bit8 | Power grid quick check abnormality |  | bit8 | Large frequency difference | For debugging
0x03 | 44 | Data 18 | Low voltage DC voltage | 2 | R | 0.01 | V |  | INT16 |  |  |  | bit7 | Diesel power supply |  | bit7 | Difference 1 | For debugging
0x03 | 45 | Data 19 | Battery SOC | 2 | R | 1 | % |  | INT16 |  |  |  | bit6 |  |  | bit6 | Frequency difference large 1 | For debugging
0x03 | 46 | Data 20 | Battery power | 2 | R | 1 | W | Positive means discharging, negative means charging | INT16 |  |  |  | bit5 | Anti-islanding frequency anomaly |  | bit5 | Output undervoltage | For debugging
0x03 | 47 | Data 21 | Photovoltaic 1 power | 2 | R | 1 | W | Positive means power generation, energy flows to the inverter | INT16 |  |  |  | bit4 |  |  | bit4
0x03 | 48 | Data 22 | Photovoltaic 2 power | 2 | R | 1 | W |  | INT16 |  |  |  | bit3 |  |  | bit3
0x03 | 49 | Data 23 |  | 2 | R |  |  |  | UINT16 |  |  |  | bit2 | Oil engine frequency abnormality |  | bit2 | Abnormal output amplitude | For debugging
0x03 | 50 | Data 24 |  | 2 | R |  |  |  | UINT16 |  |  |  | bit1 | Abnormal oil engine amplitude |  | bit1 | Abnormal output amplitude | For debugging
0x03 | 51 | Data 25 | Insulation resistance | 2 | R | 1 | k Ω |  | UINT16 |  |  |  | bit0 | Oil engine quick check abnormality |  | bit0 | Abnormal output frequency | For debugging
0x03 | 52 | Data 26 | Photovoltaic 1 stage | 2 | R |  |  |  | UINT16
0x03 | 53 | Data 27 | Photovoltaic 2-stage | 2 | R |  |  |  | UINT16
0x03 | 54 | Data 28 | Battery Stage | 2 | R |  |  |  | UINT16
0x03 | 55 | Data 29 | Battery temperature | 2 | R | 0.1 | °C |  | INT16
0x03 | 56 | Data 30 | Inversion temperature | 2 | R | 0.1 | °C |  | INT16
0x03 | 57 | Data 31 | Inverter working stage | 2 | R |  |  |  | UINT16
0x03 | 58 | Data 32 | Inductor Current | 2 | R | 0.01 | A |  | UINT16
0x03 | 59 | Data 33 | Leakage Current | 2 | R | 1 | mA |  | UINT16
0x03 | 60 | Data 34 |  | 2 | R |  |  |  | UINT16
0x03 | 61 | Data 35 | External CT current | 2 | R | 0.01 | A |  | UINT16
0x03 | 62 | Data 36 |  | 2 | R |  |  |  | UINT16
0x03 | 63 | Data 37 |  | 2 | R |  |  |  | UINT16
0x03 | 64 | Data 38 | Transformer current | 2 | R | 0.01 | A |  | UINT16
0x03 | 65 | Data 39 | Inverter active power | 2 | R | 1 | W |  | INT16
0x03 | 66 | Data 40 | Inverter reactive power | 2 | R | 1 | Var |  | INT16
0x03 | 67 | Data 41 | U PS Active Power | 2 | R | 1 | W | Positive means energy flows to the load | INT16 | UPS LOAD
0x03 | 68 | Data 42 | SMARTLOAD active power | 2 | R | 1 | W | Positive means energy flows to the load | INT16 | SMART LOAD
0x03 | 69 | Data 43 | Grid active power | 2 | R | 1 | W | Positive means buying electricity from the grid, negative means selling electricity to the grid | INT16
0x03 | 70 | Data 44 | Grid reactive power | 2 | R | 1 | Var |  | INT16
0x03 | 71 | Data 45 | Diesel engine active power | 2 | R | 1 | W | Positive means energy flows to the inverter | INT16
0x03 | 72 | Data 46 | Diesel engine reactive power | 2 | R | 1 | Var |  | INT16
0x03 | 73 | Data 47 | CT active power | 2 | R | 1 | W |  | INT16
0x03 | 74 | Data 48 | CT reactive power | 2 | R | 1 | Var |  | INT16
0x03 | 75 | Data 49 | Load active power | 2 | R | 1 | W | Positive means energy flows to the load | INT16 | HOME LOAD
0x03 | 76 | Data 50 |  | 2 | R | 1 |  |  | INT16
0x03 | 77 | Data 51 |  | 2 | R | 1 |  |  | INT16
0x03 | 78 | Data 52 |  | 2 | R | 1 |  |  | INT16
0x03 | 79 | Data 53 |  | 2 | R | 1 |  |  | INT16
0x03 | 80 | Data 54 |  | 2 | R | 1 |  |  | INT16
0x03 | 81 | Data 55 |  | 2 | R | 1 |  |  | INT16
0x03 | 82 | Data 56 |  | 2 | R | 1 |  |  | INT16
0x03 | 83 | Data 57 |  | 2 | R | 1 |  |  | INT16
0x03 | 84 | Data 58 |  | 2 | R | 1 |  |  | INT16
0x03 | 85 | Data 59 |  | 2 | R | 1 |  |  | INT16
0x03 | 86 | Data 60 |  | 2 | R | 1 |  |  | INT16
0x03 | 87 | Data 61 |  | 2 | R | 1 |  |  | INT16
0x03 | 88 | Data 62 |  | 2 | R | 1 |  |  | INT16
0x03 | 89 | Data 63 | INV software version 16-bit large version | 2 | R |  |  |  | UINT16
0x03 | 90 | Module online status |  | 2 | R |  |  | 1: Online
DC unit real-time data | [12 empty] | Table 3-1: Status information
Order | Register Address | Data Type | What the data means | Number of bytes | R/W | unit |  | Remark |  |  | 0 |  |  | 1 | 0 |  | 1 | 0
0x03 | 2000 | Status word 0 | Status Information | 2 | R |  |  | Table 3- 1 |  |  | 1 |  | bit15 |  |  | bit15
0x03 | 2001 | Status word 1 |  | 2 | R | [5 empty] | 2 |  | bit14 |  |  | bit14
0x03 | 2002 | Status word 2 |  | 2 | R | [5 empty] | 3 |  | bit13 |  |  | bit13
0x03 | 2003 | Status word 3 |  | 2 | R | [7 empty] | bit12 |  |  | bit12
0x03 | 2004 | Status word 4 |  | 2 | R | [7 empty] | bit11 |  |  | bit11
0x03 | 2005 | Status word 5 |  | 2 | R | [7 empty] | bit10 |  |  | bit10
0x03 | 2006 | Parameter 0 |  | 2 | R/W | [7 empty] | bit9 |  |  | bit9
0x03 | 2007 | Parameter 1 |  | 2 | R/W | [7 empty] | bit8 |  |  | bit8
0x03 | 2008 | Parameter 2 |  | 2 | R/W | [7 empty] | bit7 |  |  | bit7
0x03 | 2009 | Parameter 3 |  | 2 | R/W | [5 empty] | 0 |  | bit6 |  |  | bit6
0x03 | 2010 | Parameter 4 |  | 2 | R/W | [5 empty] | 1 |  | bit5 |  |  | bit5
0x03 | 2011 | Parameter 5 |  | 2 | R/W | [5 empty] | 2 |  | bit4 |  |  | bit4
0x03 | 2012 | Parameter 6 |  | 2 | R/W | [5 empty] | 3 |  | bit3 |  |  | bit3
0x03 | 2013 | Parameter 7 |  | 2 | R/W | [7 empty] | bit2 | Communication with the main DSP is abnormal |  | bit2
0x03 | 2014 | Parameter 8 |  | 2 | R/W |  |  | High 8-bit status word/low 8-bit SOC |  |  |  |  | bit1 | 12V power supply failure |  | bit1
0x03 | 2015 | Parameter 9 | Power on/off command | 2 | R/W | [7 empty] | bit0 | 24 Power failure |  | bit0
0x03 | 2016 | Parameter 10 |  | 2 | R/W
0x03 | 2017 | Parameter 11 |  | 2 | R/W | [6 empty] | 1 |  | 1 | 0 |  | 1 | 0
0x03 | 2018 | Command word 0 | Record Clearance | 2 | R/W |  |  | 1 = Clearing energy 10 = Clearing in progress 0 = Clearing completed 2 = Clearing events 20 = Clearing in progress 0 = Clearing completed |  |  | bit15 |  | bit15 |  |  | bit15
0x03 | 2019 | Command word 1 | HMI communication address | 2 | R/W |  |  | 1- 64 |  |  | bit14 |  | bit14 |  |  | bit14
0x03 | 2020 | Command word 2 | Record page number | 2 | R/W |  |  | 1- 100 |  |  | bit13 |  | bit13 |  |  | bit13
0x03 | 2021 | Command word 3 | Restore factory settings and T1 mark | 2 | R/W |  |  | 1 = Restore factory settings 2 = Mark T1 test |  |  | bit12 |  | bit12 |  |  | bit12
0x03 | 2022 | Waveform channel 0 |  | 2 | R/W | [5 empty] | bit11 |  | bit11 |  |  | bit11
0x03 | 2023 | Waveform channel 1 |  | 2 | R/W | [5 empty] | bit10 |  | bit10 |  |  | bit10
0x03 | 2024 | Waveform channel 2 |  | 2 | R/W | [5 empty] | bit9 |  | bit9 |  |  | bit9
0x03 | 2025 | Waveform channel 3 |  | 2 | R/W | [5 empty] | bit8 |  | bit8 |  |  | bit8
0x03 | 2026 | Data0 | 24V voltage | 2 | R |  |  |  | INT16 |  | bit7 |  | bit7 |  |  | bit7
0x03 | 2027 | Data 1 | 12V voltage | 2 | R |  |  |  | INT16 |  | bit6 |  | bit6 |  |  | bit6
0x03 | 2028 | Data 2 | Leakage current (effective value) | 2 | R |  |  |  | INT16 |  | bit5 |  | bit5 |  |  | bit5
0x03 | 2029 | Data 3 | Leakage current (level) | 2 | R |  |  |  | INT16 |  | bit4 |  | bit4 |  |  | bit4
0x03 | 2030 | Data 4 |  | 2 | R |  |  |  | INT16 |  | bit3 |  | bit3 |  |  | bit3
0x03 | 2031 | Data 5 |  | 2 | R |  |  |  | INT16 |  | bit2 |  | bit2 |  |  | bit2
0x03 | 2032 | Data 6 |  | 2 | R |  |  |  | INT16 |  | bit1 |  | bit1 |  |  | bit1
0x03 | 2033 | Data 7 |  | 2 | R |  |  |  | INT16 |  | bit0 |  | bit0 |  |  | bit0
0x03 | 2034 | Data 8 |  | 2 | R |  |  |  | INT16 |  | Table 10 Machine operation status |  | Table 1-5: SOC state
0x03 | 2035 | Data 9 |  | 2 | R |  |  |  | INT16 |  |  |  |  | 1 | 0
0x03 | 2036 | Data 10 | Substrate temperature 1 | 2 | R |  |  |  | INT16 |  | bit15 | reserve | bit15 | Charging Enable
0x03 | 2037 | Data 11 | Substrate temperature 2 | 2 | R |  |  |  | INT16 |  | bit14 | reserve | bit14 | Discharge Enable
0x03 | 2038 | Data 12 | Substrate temperature 3 | 2 | R |  |  |  | INT16 |  | bit13 | reserve | bit13
0x03 | 2039 | Data 13 | Substrate temperature 4 | 2 | R | [5 empty] | bit12 | reserve | bit12
0x03 | 2040 | Data 14 | Radiator temperature 1 | 2 | R | [5 empty] | bit11 | reserve | bit11
0x03 | 2041 | Data 15 | Radiator temperature 2 | 2 | R | [5 empty] | bit10 | reserve | bit10
0x03 | 2042 | Data 16 | Radiator temperature 3 | 2 | R | [5 empty] | bit9 | reserve | bit9
0x03 | 2043 | Data 17 | Radiator temperature 4 | 2 | R | [5 empty] | bit8 | reserve | bit8 | Communication with BMS is normal
0x03 | 2044 | Data 18 | The lower 8-bit minor version of the slave MCU software version | 2 | R | [5 empty] | bit7 | 0 = Standby 1= Self-Test 2= normal 3= Alerts 4= Fault 5= Shutdown | bit7 | S OC value
0x03 | 2045 | Data 19 | Sub-MCU software version 16-bit large version | 2 | R | [5 empty] | bit6 |  | bit6
0x03 | 2046 | Data 20 |  | 2 | R | [5 empty] | bit5 |  | bit5
0x03 | 2047 | Data 21 |  | 2 | R | [5 empty] | bit4 |  | bit4
0x03 | 2048 | Data 22 |  | 2 | R | [5 empty] | bit3 |  | bit3
0x03 | 2049 | Data 23 |  | 2 | R | [5 empty] | bit2 |  | bit2
0x03 | 2050 | Data 24 |  | 2 | R | [5 empty] | bit1 |  | bit1
0x03 | 2051 | Data 25 | T1 test logo | 2 | R |  |  | 16=Already T1 tested |  |  | bit0 |  | bit0
0x03 | 2052 | Data 26 |  | 2 | R
0x03 | 2053 | Data 27 |  | 2 | R |  |  |  | UINT16
0x03 | 2054 | Data 28 |  | 2 | R |  |  |  | UINT16
0x03 | 2055 | Data 29 | Battery radiator temperature | 2 | R | 1 | °C |  | UINT16
0x03 | 2056 | Data 30 | Inverter radiator temperature | 2 | R |  |  |  | UINT16
0x03 | 2057 | Data 31 | Working stage | 2 | R |  |  |  | UINT16
0x03 | 2058 | Data 32 | Machine operating status | 2 | R |  |  | Table 1 0 | UINT16
0x03 | 2059 | Data 33 |  | 2 | R
0x03 | 2060 | Data 34 |  | 2 | R
0x03 | 2061 | Data 35 | Alarm status word 1 | 2 | R |  |  | See fault information table | UINT16
0x03 | 2062 | Data 36 | Alarm status word 2 | 2 | R |  |  |  | UINT16
0x03 | 2063 | Data 37 | Fault status word 1 | 2 | R |  |  |  | UINT16
0x03 | 2064 | Data 38 | Fault status word 2 | 2 | R |  |  |  | UINT16
0x03 | 2065 | Data 39 | Photovoltaic power generation on the day | 2 | R | 0.1 | k W |  | UINT16
0x03 | 2066 | Data 40 | Total photovoltaic power generation | 2 | R | 0.1 | k W | High 1 6-digit | UINT16
0x03 | 2067 | Data 41 |  | 2 | R |  | k W | Low 1 6-digit | UINT16
0x03 | 2068 | Data 42 | Battery charge level for the day | 2 | R | 0.1 | k W |  | UINT16
0x03 | 2069 | Data 43 | Total battery charge | 2 | R | 0.1 | k W | High 1 6-digit | UINT16
0x03 | 2070 | Data 44 |  | 2 | R |  | k W | Low 1 6-digit | UINT16
0x03 | 2071 | Data 45 | Battery discharge on the day | 2 | R | 0.1 | k W |  | UINT16
0x03 | 2072 | Data 46 | Total battery discharge | 2 | R | 0.1 | k W | High 1 6-digit | UINT16
0x03 | 2073 | Data 47 |  | 2 | R |  | k W | Low 1 6-digit | UINT16
0x03 | 2074 | Data 48 | The power grid purchased electricity on that day | 2 | R | 0.1 | k W |  | UINT16
0x03 | 2075 | Data 49 | Total power grid purchase electricity | 2 | R | 0.1 | k W | High 1 6-digit | UINT16
0x03 | 2076 | Data 50 |  | 2 | R |  | k W | Low 1 6-digit | UINT16
0x03 | 2077 | Data 51 | The power grid sold electricity on that day | 2 | R | 0.1 | k W |  | UINT16
0x03 | 2078 | Data 52 | Total power grid sold electricity | 2 | R | 0.1 | k W | High 1 6-digit | UINT16
0x03 | 2079 | Data 53 |  | 2 | R |  | k W | Low 1 6-digit | UINT16
0x03 | 2080 | Data 54 | Load power consumption on the day | 2 | R | 0.1 | k W |  | UINT16
0x03 | 2081 | Data 55 | Total load total power consumption | 2 | R | 0.1 | k W | High 1 6-digit | UINT16
0x03 | 2082 | Data 56 |  | 2 | R |  | k W | Low 1 6-digit | UINT16
0x03 | 2083 | Data 57 |  | 2 | R
0x03 | 2084 | Data 58 |  | 2 | R
0x03 | 2085 | Data 59 |  | 2 | R
0x03 | 2086 | Data 60 |  | 2 | R
0x03 | 2087 | Data 61 |  | 2 | R
0x03 | 2088 | Data 62 |  | 2 | R |  |  |  | UINT16
0x03 | 2089 | Data 63 |  | 2 | R |  |  |  | UINT16
0x03 | 2090 | Module online status |  | 2 | R |  |  | 1: Online | UINT16

## Parameter Group
Inverter unit parameter address
Order | Register Address | Parameter Group | Serial number | Data Type | Number of bytes | R/W | unit |  | Parameter Description | scope
0x03 | 640 | Group 0 | 0 | Parameter 0 | 2 | R/W |  |  | Parameter page number | 0
0x03 | 641 |  | 1 | Parameter 1 | 2 | R/W |  |  | Mailing address 1 | 0~63 odd number | Com Addr
0x03 | 642 |  | 2 | Parameter 2 | 2 | R/W |  |  | Inverter rated voltage | 2200 | INV Rated Voltage
0x03 | 643 |  | 3 | Parameter 3 | 2 | R/W |  |  | Inverter rated frequency | 5000 | INV Rated Freq
0x03 | 644 |  | 4 | Parameter 4 | 2 | R/W |  |  | Maximum grid-connected current |  | Max INV Current
0x03 | 645 |  | 5 | Parameter 5 | 2 | R/W |  |  | Maximum grid voltage
0x03 | 646 |  | 6 | Parameter 6 | 2 | R/W |  |  | Minimum grid voltage
0x03 | 647 |  | 7 | Parameter 7 | 2 | R/W |  |  | Maximum grid frequency |  | The Range of V_grid
0x03 | 648 |  | 8 | Parameter 8 | 2 | R/W |  |  | Minimum grid frequency
0x03 | 649 |  | 9 | Parameter 9 | 2 | R/W |  |  | Maximum frequency of oil engine
0x03 | 650 |  | 10 | Parameter 10 | 2 | R/W |  |  | Minimum frequency of oil engine
0x03 | 651 |  | 11 | Parameter 11 | 2 | R/W |  |  | Correspondence address 2 | 0~63 odd number
0x03 | 652 |  | 12 | Parameter 12 | 2 | R/W |  |  | Maximum voltage of oil engine
0x03 | 653 |  | 13 | Parameter 13 | 2 | R/W |  |  | Minimum voltage of oil generator
0x03 | 654 | Group 1 | 14 | Parameter 0 | 2 | R/W |  |  | Parameter page number | 1
0x03 | 655 |  | 15 | Parameter 1 | 2 | R/W |  |  | Set year data | 0~99
0x03 | 656 |  | 16 | Parameter 2 | 2 | R/W |  |  | Set monthly data | 1~12
0x03 | 657 |  | 17 | Parameter 3 | 2 | R/W |  |  | Set weekly data | 1~7
0x03 | 658 |  | 18 | Parameter 4 | 2 | R/W |  |  | Set daily data | 1~31
0x03 | 659 |  | 19 | Parameter 5 | 2 | R/W |  |  | Setting time data | 0~23
0x03 | 660 |  | 20 | Parameter 6 | 2 | R/W |  |  | Set the sub-data | 0~59
0x03 | 661 |  | 21 | Parameter 7 | 2 | R/W |  |  | Set the seconds data | 0~59
0x03 | 662 |  | 22 | Parameter 8 | 2 | R/W |  |  | Startup Settings | 16
0x03 | 663 |  | 23 | Parameter 9 | 2 | R/W
0x03 | 664 |  | 24 | Parameter 10 | 2 | R/W
0x03 | 665 |  | 25 | Parameter 11 | 2 | R/W
0x03 | 666 |  | 26 | Parameter 12 | 2 | R/W
0x03 | 667 |  | 27 | Parameter 13 | 2 | R/W
0x03 | 668 | Group 2 | 28 | Parameter 0 | 2 | R/W |  |  | Parameter page number | 2
0x03 | 669 |  | 29 | Parameter 1 | 2 | R/W
0x03 | 670 |  | 30 | Parameter 2 | 2 | R/W
0x03 | 671 |  | 31 | Parameter 3 | 2 | R/W
0x03 | 672 |  | 32 | Parameter 4 | 2 | R/W
0x03 | 673 |  | 33 | Parameter 5 | 2 | R/W
0x03 | 674 |  | 34 | Parameter 6 | 2 | R/W
0x03 | 675 |  | 35 | Parameter 7 | 2 | R/W
0x03 | 676 |  | 36 | Parameter 8 | 2 | R/W
0x03 | 677 |  | 37 | Parameter 9 | 2 | R/W
0x03 | 678 |  | 38 | Parameter 10 | 2 | R/W
0x03 | 679 |  | 39 | Parameter 11 | 2 | R/W
0x03 | 680 |  | 40 | Parameter 12 | 2 | R/W
0x03 | 681 |  | 41 | Parameter 13 | 2 | R/W
0x03 | 682 | Group 3 | 42 | Parameter 0 | 2 | R/W |  |  | Parameter page number | 3
0x03 | 683 |  | 43 | Parameter 1 | 2 | R/W
0x03 | 684 |  | 44 | Parameter 2 | 2 | R/W
0x03 | 685 |  | 45 | Parameter 3 | 2 | R/W
0x03 | 686 |  | 46 | Parameter 4 | 2 | R/W
0x03 | 687 |  | 47 | Parameter 5 | 2 | R/W
0x03 | 688 |  | 48 | Parameter 6 | 2 | R/W
0x03 | 689 |  | 49 | Parameter 7 | 2 | R/W
0x03 | 690 |  | 50 | Parameter 8 | 2 | R/W
0x03 | 691 |  | 51 | Parameter 9 | 2 | R/W
0x03 | 692 |  | 52 | Parameter 10 | 2 | R/W
0x03 | 693 |  | 53 | Parameter 11 | 2 | R/W
0x03 | 694 |  | 54 | Parameter 12 | 2 | R/W
0x03 | 695 |  | 55 | Parameter 13 | 2 | R/W
0x03 | 696 | Group 4 | 56 | Parameter 0 | 2 | R/W |  |  | Parameter page number | 4
0x03 | 697 |  | 57 | Parameter 1 | 2 | R/W | 1 |  | Bypass initialization settings
0x03 | 698 |  | 58 | Parameter 2 | 2 | R/W | 1 |  | Oil engine settings
0x03 | 699 |  | 59 | Parameter 3 | 2 | R/W | 1 |  | Automatic power-on enable | 5= Enable
0x03 | 700 |  | 60 | Parameter 4 | 2 | R/W | 1 |  | Maximum power selling
0x03 | 701 |  | 61 | Parameter 5 | 2 | R/W |  |  | Oil engine interface type | 5=smart 10=AC Couple Other = Diesel
0x03 | 702 |  | 62 | Parameter 6 | 2 | R/W |  |  | Smart Mode (always on) | 0x05=Ongrid always On Enable 0x50=only bat on Enable
0x03 | 703 |  | 63 | Parameter 7 | 2 | R/W |  |  | Oil engine start signal enable | 0x05=Gen Start Enable Other = Prohibited
0x03 | 704 |  | 64 | Parameter 8 | 2 | R/W | 0.01
0x03 | 705 |  | 65 | Parameter 9 | 2 | R/W |  |  | Diesel engine mode | 5=VF model Other = PQ mode
0x03 | 706 |  | 66 | Parameter 10 | 2 | R/W |  |  | Number of parallel units | 0=single machine>0=number of parallel machines
0x03 | 707 |  | 67 | Parameter 11 | 2 | R/W |  |  | DC bus control mode | Debug, default 0
0x03 | 708 |  | 68 | Parameter 12 | 2 | R/W |  |  | External Current Hall Rating | 100
0x03 | 709 |  | 69 | Parameter 13 | 2 | R/W |  |  | Current Control Mode | 1= CT
0x03 | 710 | Group 5 | 70 | Parameter 0 | 2 | R/W |  |  | Parameter page number | 5
0x03 | 711 |  | 71 | Parameter 1 | 2 | R/W
0x03 | 712 |  | 72 | Parameter 2 | 2 | R/W
0x03 | 713 |  | 73 | Parameter 3 | 2 | R/W
0x03 | 714 |  | 74 | Parameter 4 | 2 | R/W
0x03 | 715 |  | 75 | Parameter 5 | 2 | R/W
0x03 | 716 |  | 76 | Parameter 6 | 2 | R/W
0x03 | 717 |  | 77 | Parameter 7 | 2 | R/W
0x03 | 718 |  | 78 | Parameter 8 | 2 | R/W
0x03 | 719 |  | 79 | Parameter 9 | 2 | R/W
0x03 | 720 |  | 80 | Parameter 10 | 2 | R/W
0x03 | 721 |  | 81 | Parameter 11 | 2 | R/W
0x03 | 722 |  | 82 | Parameter 12 | 2 | R/W
0x03 | 723 |  | 83 | Parameter 13 | 2 | R/W
0x03 | 724 | Group 6 | 84 | Parameter 0 | 2 | R/W |  |  | Parameter page number | 6
0x03 | 725 |  | 85 | Parameter 1 | 2 | R/W
0x03 | 726 |  | 86 | Parameter 2 | 2 | R/W
0x03 | 727 |  | 87 | Parameter 3 | 2 | R/W
0x03 | 728 |  | 88 | Parameter 4 | 2 | R/W
0x03 | 729 |  | 89 | Parameter 5 | 2 | R/W
0x03 | 730 |  | 90 | Parameter 6 | 2 | R/W
0x03 | 731 |  | 91 | Parameter 7 | 2 | R/W
0x03 | 732 |  | 92 | Parameter 8 | 2 | R/W
0x03 | 733 |  | 93 | Parameter 9 | 2 | R/W
0x03 | 734 |  | 94 | Parameter 10 | 2 | R/W
0x03 | 735 |  | 95 | Parameter 11 | 2 | R/W
0x03 | 736 |  | 96 | Parameter 12 | 2 | R/W
0x03 | 737 |  | 97 | Parameter 13 | 2 | R/W
0x03 | 738 | Group 7 | 98 | Parameter 0 | 2 | R/W |  |  | Parameter page number | 7
0x03 | 739 |  | 99 | Parameter 1 | 2 | R/W
0x03 | 740 |  | 100 | Parameter 2 | 2 | R/W
0x03 | 741 |  | 101 | Parameter 3 | 2 | R/W
0x03 | 742 |  | 102 | Parameter 4 | 2 | R/W
0x03 | 743 |  | 103 | Parameter 5 | 2 | R/W
0x03 | 744 |  | 104 | Parameter 6 | 2 | R/W
0x03 | 745 |  | 105 | Parameter 7 | 2 | R/W
0x03 | 746 |  | 106 | Parameter 8 | 2 | R/W
0x03 | 747 |  | 107 | Parameter 9 | 2 | R/W
0x03 | 748 |  | 108 | Parameter 10 | 2 | R/W
0x03 | 749 |  | 109 | Parameter 11 | 2 | R/W
0x03 | 750 |  | 110 | Parameter 12 | 2 | R/W
0x03 | 751 |  | 111 | Parameter 13 | 2 | R/W
0x03 | 1504 | Group 8 | 0 | Parameter 0 | 2 | R/W |  |  | Parameter page number | 8
0x03 | 1505 |  | 1 | Parameter 1 | 2 | R/W | 0.1 |  | Positive DC bus bias | '-100~100
0x03 | 1506 |  | 2 | Parameter 2 | 2 | R/W | 0.0001 |  | Positive DC bus slope | '-1000~1000
0x03 | 1507 |  | 3 | Parameter 3 | 2 | R/W | 0.1 |  | Negative DC bus bias | '-100~100
0x03 | 1508 |  | 4 | Parameter 4 | 2 | R/W | 0.0001 |  | Negative DC bus slope | '-1000~1000
0x03 | 1509 |  | 5 | Parameter 5 | 2 | R/W | 0.1 |  | Inverter voltage A slope | '-1000~1000
0x03 | 1510 |  | 6 | Parameter 6 | 2 | R/W | 0.0001 |  | Inverter voltage B slope | '-1000~1000
0x03 | 1511 |  | 7 | Parameter 7 | 2 | R/W | 0.1 |  | Inverter voltage C slope | '-1000~1000
0x03 | 1512 |  | 8 | Parameter 8 | 2 | R/W | 0.0001 |  | Output voltage A slope | '-1000~1000
0x03 | 1513 |  | 9 | Parameter 9 | 2 | R/W | 0.1 |  | Output voltage B slope | '-1000~1000
0x03 | 1514 |  | 10 | Parameter 10 | 2 | R/W | 0.0001 |  | Output voltage C slope | '-1000~1000
0x03 | 1515 |  | 11 | Parameter 11 | 2 | R/W | 0.1 |  | Phase A bypass voltage slope | '-100~100
0x03 | 1516 |  | 12 | Parameter 12 | 2 | R/W | 0.0001 |  | Phase B bypass voltage slope | '-1000~1000
0x03 | 1517 |  | 13 | Parameter 13 | 2 | R/W |  |  | Phase C bypass voltage slope
0x03 | 1518 | Group 9 | 14 | Parameter 0 | 2 | R/W |  |  | Parameter page number | 9
0x03 | 1519 |  | 15 | Parameter 1 | 2 | R/W | 0.1 |  | A phase diesel generator voltage slope | '-100~100
0x03 | 1520 |  | 16 | Parameter 2 | 2 | R/W | 0.0001 |  | B phase diesel generator voltage slope | '-1000~1000
0x03 | 1521 |  | 17 | Parameter 3 | 2 | R/W | 0.1 |  | C phase diesel generator voltage slope | '-100~100
0x03 | 1522 |  | 18 | Parameter 4 | 2 | R/W | 0.0001 |  |  | '-1000~1000
0x03 | 1523 |  | 19 | Parameter 5 | 2 | R/W | 0.0001 |  | Phase A CT current slope | '-1000~1000
0x03 | 1524 |  | 20 | Parameter 6 | 2 | R/W | 0.0001 |  | Phase B CT current slope | '-1000~1000
0x03 | 1525 |  | 21 | Parameter 7 | 2 | R/W | 0.0001 |  | Phase C CT current slope | '-1000~1000
0x03 | 1526 |  | 22 | Parameter 8 | 2 | R/W | 0.0001 |  | A phase diesel generator current slope | '-1000~1000
0x03 | 1527 |  | 23 | Parameter 9 | 2 | R/W | 0.0001 |  | B phase diesel generator current slope | '-1000~1000
0x03 | 1528 |  | 24 | Parameter 10 | 2 | R/W | 0.0001 |  | C phase diesel generator current slope | '-1000~1000
0x03 | 1529 |  | 25 | Parameter 11 | 2 | R/W |  |  | reserve
0x03 | 1530 |  | 26 | Parameter 12 | 2 | R/W |  |  | reserve
0x03 | 1531 |  | 27 | Parameter 13 | 2 | R/W |  |  | reserve
0x03 | 1532 | Group 1 0 | 28 | Parameter 0 | 2 | R/W |  |  | Parameter page number | 10
0x03 | 1533 |  | 29 | Parameter 1 | 2 | R/W | 0.0001 |  | Phase A inductor current slope | '-1000~1000
0x03 | 1534 |  | 30 | Parameter 2 | 2 | R/W | 0.0001 |  | Phase B inductor current slope | '-1000~1000
0x03 | 1535 |  | 31 | Parameter 3 | 2 | R/W | 0.0001 |  | Phase C inductor current slope | '-1000~1000
0x03 | 1536 |  | 32 | Parameter 4 | 2 | R/W | 0.0001 |  | A phase output current slope | '-1000~1000
0x03 | 1537 |  | 33 | Parameter 5 | 2 | R/W | 0.0001 |  | B phase output current slope | '-1000~1000
0x03 | 1538 |  | 34 | Parameter 6 | 2 | R/W | 0.0001 |  | C phase output current slope | '-1000~1000
0x03 | 1539 |  | 35 | Parameter 7 | 2 | R/W | 0.0001 |  | Phase A grid current slope | '-1000~1000
0x03 | 1540 |  | 36 | Parameter 8 | 2 | R/W | 0.0001 |  | Phase B grid current slope | '-1000~1000
0x03 | 1541 |  | 37 | Parameter 9 | 2 | R/W | 0.0001 |  | Phase C grid current slope | '-1000~1000
0x03 | 1542 |  | 38 | Parameter 10 | 2 | R/W | 0.0001 |  | A phase load current slope | '-1000~1000
0x03 | 1543 |  | 39 | Parameter 11 | 2 | R/W | 0.0001 |  | Phase B load current slope | '-1000~1000
0x03 | 1544 |  | 40 | Parameter 12 | 2 | R/W | 0.0001 |  | Phase C load current slope | '-1000~1000
0x03 | 1545 |  | 41 | Parameter 13 | 2 | R/W |  |  | reserve
0x03 | 1546 | Group 1 1 | 42 | Parameter 0 | 2 | R/W |  |  | Parameter page number | 11
0x03 | 1547 |  | 43 | Parameter 1 | 2 | R/W | 0.0001
0x03 | 1548 |  | 44 | Parameter 2 | 2 | R/W | 0.0001
0x03 | 1549 |  | 45 | Parameter 3 | 2 | R/W | 0.0001
0x03 | 1550 |  | 46 | Parameter 4 | 2 | R/W | 0.0001
0x03 | 1551 |  | 47 | Parameter 5 | 2 | R/W | 0.0001
0x03 | 1552 |  | 48 | Parameter 6 | 2 | R/W | 0.0001
0x03 | 1553 |  | 49 | Parameter 7 | 2 | R/W | 0.0001
0x03 | 1554 |  | 50 | Parameter 8 | 2 | R/W | 0.0001
0x03 | 1555 |  | 51 | Parameter 9 | 2 | R/W | 0.0001
0x03 | 1556 |  | 52 | Parameter 10 | 2 | R/W | 0.0001
0x03 | 1557 |  | 53 | Parameter 11 | 2 | R/W | 0.0001
0x03 | 1558 |  | 54 | Parameter 12 | 2 | R/W | 0.0001
0x03 | 1559 |  | 55 | Parameter 13 | 2 | R/W |  |  | reserve
0x03 | 1560 | Group 1 2 | 56 | Parameter 0 | 2 | R/W |  |  | Parameter page number | 12
0x03 | 1561 |  | 57 | Parameter 1 | 2 | R/W
0x03 | 1562 |  | 58 | Parameter 2 | 2 | R/W
0x03 | 1563 |  | 59 | Parameter 3 | 2 | R/W
0x03 | 1564 |  | 60 | Parameter 4 | 2 | R/W
0x03 | 1565 |  | 61 | Parameter 5 | 2 | R/W
0x03 | 1566 |  | 62 | Parameter 6 | 2 | R/W
0x03 | 1567 |  | 63 | Parameter 7 | 2 | R/W
0x03 | 1568 |  | 64 | Parameter 8 | 2 | R/W
0x03 | 1569 |  | 65 | Parameter 9 | 2 | R/W
0x03 | 1570 |  | 66 | Parameter 10 | 2 | R/W
0x03 | 1571 |  | 67 | Parameter 11 | 2 | R/W
0x03 | 1572 |  | 68 | Parameter 12 | 2 | R/W
0x03 | 1573 |  | 69 | Parameter 13 | 2 | R/W
0x03 | 1574 | Group 1 3 | 70 | Parameter 0 | 2 | R/W |  |  | Parameter page number | 13
0x03 | 1575 |  | 71 | Parameter 1 | 2 | R/W
0x03 | 1576 |  | 72 | Parameter 2 | 2 | R/W
0x03 | 1577 |  | 73 | Parameter 3 | 2 | R/W
0x03 | 1578 |  | 74 | Parameter 4 | 2 | R/W
0x03 | 1579 |  | 75 | Parameter 5 | 2 | R/W
0x03 | 1580 |  | 76 | Parameter 6 | 2 | R/W
0x03 | 1581 |  | 77 | Parameter 7 | 2 | R/W
0x03 | 1582 |  | 78 | Parameter 8 | 2 | R/W
0x03 | 1583 |  | 79 | Parameter 9 | 2 | R/W
0x03 | 1584 |  | 80 | Parameter 10 | 2 | R/W
0x03 | 1585 |  | 81 | Parameter 11 | 2 | R/W
0x03 | 1586 |  | 82 | Parameter 12 | 2 | R/W
0x03 | 1587 |  | 83 | Parameter 13 | 2 | R/W
0x03 | 1588 | Group 1 4 | 84 | Parameter 0 | 2 | R/W |  |  | Parameter page number | 14
0x03 | 1589 |  | 85 | Parameter 1 | 2 | R/W
0x03 | 1590 |  | 86 | Parameter 2 | 2 | R/W
0x03 | 1591 |  | 87 | Parameter 3 | 2 | R/W
0x03 | 1592 |  | 88 | Parameter 4 | 2 | R/W
0x03 | 1593 |  | 89 | Parameter 5 | 2 | R/W
0x03 | 1594 |  | 90 | Parameter 6 | 2 | R/W
0x03 | 1595 |  | 91 | Parameter 7 | 2 | R/W
0x03 | 1596 |  | 92 | Parameter 8 | 2 | R/W
0x03 | 1597 |  | 93 | Parameter 9 | 2 | R/W
0x03 | 1598 |  | 94 | Parameter 10 | 2 | R/W
0x03 | 1599 |  | 95 | Parameter 11 | 2 | R/W
0x03 | 1600 |  | 96 | Parameter 12 | 2 | R/W
0x03 | 1601 |  | 97 | Parameter 13 | 2 | R/W
0x03 | 1602 | Group 1 5 | 98 | Parameter 0 | 2 | R/W |  |  | Parameter page number | 15
0x03 | 1603 |  | 99 | Parameter 1 | 2 | R/W
0x03 | 1604 |  | 100 | Parameter 2 | 2 | R/W
0x03 | 1605 |  | 101 | Parameter 3 | 2 | R/W
0x03 | 1606 |  | 102 | Parameter 4 | 2 | R/W
0x03 | 1607 |  | 103 | Parameter 5 | 2 | R/W
0x03 | 1608 |  | 104 | Parameter 6 | 2 | R/W
0x03 | 1609 |  | 105 | Parameter 7 | 2 | R/W
0x03 | 1610 |  | 106 | Parameter 8 | 2 | R/W
0x03 | 1611 |  | 107 | Parameter 9 | 2 | R/W
0x03 | 1612 |  | 108 | Parameter 10 | 2 | R/W
0x03 | 1613 |  | 109 | Parameter 11 | 2 | R/W
0x03 | 1614 |  | 110 | Parameter 12 | 2 | R/W |  |  |  | 0
0x03 | 1615 |  | 111 | Parameter 13 | 2 | R/W |  |  | K12=156 , K13=189 Online Upgrade | 0
DC unit parameter address
Order | Register Address | Parameter Group | Serial number | Data Type | Number of bytes | R/W | unit |  | Parameter Description | scope
0x03 | 2640 | Group 0 | 0 | Parameter 0 | 2 | R/W |  |  | Parameter page number | 0
0x03 | 2641 |  | 1 | Parameter 1 | 2 | R/W |  |  | Mailing address 1 | 0~63 even | Com Addr
0x03 | 2642 |  | 2 | Parameter 2 | 2 | R/W |  |  | Maximum battery voltage | 4800~6500 | Max V_charge Of BAT
0x03 | 2643 |  | 3 | Parameter 3 | 2 | R/W |  |  | Minimum battery voltage | 3500-~4000 | Min V_discharge Of BAT
0x03 | 2644 |  | 4 | Parameter 4 | 2 | R/W |  |  | Maximum battery charging current | 0~3000 | Battery Capacity
0x03 | 2645 |  | 5 | Parameter 5 | 2 | R/W |  |  | Maximum battery discharge current | 0~3000 | Max I_charge Of BAT
0x03 | 2646 |  | 6 | Parameter 6 | 2 | R/W | 1 | AH | Battery capacity | 10~2000 | Min I_discharge Of BAT
0x03 | 2647 |  | 7 | Parameter 7 | 2 | R/W |  |  | Photovoltaic 1 maximum voltage | 1600~8000 | Max Voltage Of PV1
0x03 | 2648 |  | 8 | Parameter 8 | 2 | R/W |  |  | Photovoltaic 1 maximum current | 0~2600 | Max Current Of PV1
0x03 | 2649 |  | 9 | Parameter 9 | 2 | R/W |  |  | Photovoltaic 2 maximum voltage | 1600~8000 | Max Voltage Of PV2
0x03 | 2650 |  | 10 | Parameter 10 | 2 | R/W |  |  | Photovoltaic 2 maximum current | 0~1700 | Max Current Of PV2
0x03 | 2651 |  | 11 | Parameter 11 | 2 | R/W |  |  | Correspondence address 2 | 0~63 even
0x03 | 2652 |  | 12 | Parameter 12 | 2 | R/W |  |  | Battery Type | 0x5- Lithium battery; 0x50- Non-lithium battery (voltage control)
0x03 | 2653 |  | 13 | Parameter 13 | 2 | R/W
0x03 | 2654 | Group 1 | 14 | Parameter 0 | 2 | R/W |  |  |  | 1
0x03 | 2655 |  | 15 | Parameter 1 | 2 | R/W |  |  | Maximum power of grid discharge | AC side power
0x03 | 2656 |  | 16 | Parameter 2 | 2 | R/W |  |  | Grid discharge minimum SOC
0x03 | 2657 |  | 17 | Parameter 3 | 2 | R/W |  |  | Maximum SOC for grid charging
0x03 | 2658 |  | 18 | Parameter 4 | 2 | R/W |  |  | Grid discharge minimum voltage
0x03 | 2659 |  | 19 | Parameter 5 | 2 | R/W |  |  | Maximum voltage for grid charging
0x03 | 2660 |  | 20 | Parameter 6 | 2 | R/W |  |  | Maximum charging current of the power grid | Battery side
0x03 | 2661 |  | 21 | Parameter 7 | 2 | R/W |  |  | Maximum diesel charging current
0x03 | 2662 |  | 22 | Parameter 8 | 2 | R/W |  |  | Maximum discharge power of oil engine
0x03 | 2663 |  | 23 | Parameter 9 | 2 | R/W |  |  | Minimum SOC of oil engine discharge
0x03 | 2664 |  | 24 | Parameter 10 | 2 | R/W |  |  | Maximum SOC of diesel engine charging
0x03 | 2665 |  | 25 | Parameter 11 | 2 | R/W |  |  | Minimum discharge voltage of oil engine
0x03 | 2666 |  | 26 | Parameter 12 | 2 | R/W |  |  | Maximum voltage for diesel engine charging
0x03 | 2667 |  | 27 | Parameter 13 | 2 | R/W |  |  | The grid prohibits charging at the minimum SOC
0x03 | 2668 | Group 2 | 28 | Parameter 0 | 2 | R/W |  |  | Parameter page number | 2
0x03 | 2669 |  | 29 | Parameter 1 | 2 | R/W |  |  | Power control time 1 | 0~2359
0x03 | 2670 |  | 30 | Parameter 2 | 2 | R/W |  |  | Power control time 2 | 0~2359
0x03 | 2671 |  | 31 | Parameter 3 | 2 | R/W |  |  | Power control time 3 | 0~2359
0x03 | 2672 |  | 32 | Parameter 4 | 2 | R/W |  |  | Power control time 4 | 0~2359
0x03 | 2673 |  | 33 | Parameter 5 | 2 | R/W |  |  | Power control time 5 | 0~2359
0x03 | 2674 |  | 34 | Parameter 6 | 2 | R/W |  |  | Power control time 6 | 0~2359
0x03 | 2675 |  | 35 | Parameter 7 | 2 | R/W |  |  | Power control time 7 | 0~2359
0x03 | 2676 |  | 36 | Parameter 8 | 2 | R/W |  |  | Power control time 8 | 0~2359
0x03 | 2677 |  | 37 | Parameter 9 | 2 | R/W |  |  | Grid charging enable flag |  | bit=1 enables
0x03 | 2678 |  | 38 | Parameter 10 | 2 | R/W |  |  | Engine charging enable flag
0x03 | 2679 |  | 39 | Parameter 11 | 2 | R/W
0x03 | 2680 |  | 40 | Parameter 12 | 2 | R/W
0x03 | 2681 |  | 41 | Parameter 13 | 2 | R/W
0x03 | 2682 | Group 3 | 42 | Parameter 0 | 2 | R/W |  |  | Parameter page number | 3
0x03 | 2683 |  | 43 | Parameter 1 | 2 | R/W |  |  | 0 Point to control time 1 Power | 0~+12000
0x03 | 2684 |  | 44 | Parameter 2 | 2 | R/W |  |  | Control time 1 To control time 2 Power | 0~+12000
0x03 | 2685 |  | 45 | Parameter 3 | 2 | R/W |  |  | Control time 2 To control time 3 Power | 0~+12000
0x03 | 2686 |  | 46 | Parameter 4 | 2 | R/W |  |  | Control time 3 To control time 4 Power | 0~+12000
0x03 | 2687 |  | 47 | Parameter 5 | 2 | R/W |  |  | Control time 4 To control time 5 Power | 0~+12000
0x03 | 2688 |  | 48 | Parameter 6 | 2 | R/W |  |  | Control time5 To control time 6 Power | 0~+12000
0x03 | 2689 |  | 49 | Parameter 7 | 2 | R/W |  |  | Control time 6 To control time 7 Power | 0~+12000
0x03 | 2690 |  | 50 | Parameter 8 | 2 | R/W |  |  | Control time 7 To control time 8 Power | 0~+12000
0x03 | 2691 |  | 51 | Parameter 9 | 2 | R/W |  |  | Control time 8 arrive twenty three : 59 Power | 0~+12000
0x03 | 2692 |  | 52 | Parameter 10 | 2 | R/W
0x03 | 2693 |  | 53 | Parameter 11 | 2 | R/W
0x03 | 2694 |  | 54 | Parameter 12 | 2 | R/W
0x03 | 2695 |  | 55 | Parameter 13 | 2 | R/W
0x03 | 2696 | Group 4 | 56 | Parameter 0 | 2 | R/W |  |  | Parameter page number | 4
0x03 | 2697 |  | 57 | Parameter 1 | 2 | R/W | 1 |  | 0 Point to control time 1 of SOC
0x03 | 2698 |  | 58 | Parameter 2 | 2 | R/W | 1 |  | Control time 1 To control time 2 SOC
0x03 | 2699 |  | 59 | Parameter 3 | 2 | R/W | 1 |  | Control time 2 To control time 3 SOC
0x03 | 2700 |  | 60 | Parameter 4 | 2 | R/W | 1 |  | Control time 3 To control time 4 SOC
0x03 | 2701 |  | 61 | Parameter 5 | 2 | R/W |  |  | Control time 4 To control time 5 SOC
0x03 | 2702 |  | 62 | Parameter 6 | 2 | R/W |  |  | Control time 5 To control time 6 SOC
0x03 | 2703 |  | 63 | Parameter 7 | 2 | R/W |  |  | Control time 6 To control time 7 SOC
0x03 | 2704 |  | 64 | Parameter 8 | 2 | R/W | 0.01 |  | Control time 7 To control time 8 SOC
0x03 | 2705 |  | 65 | Parameter 9 | 2 | R/W |  |  | Control time 8 arrive twenty three : 59 SOC
0x03 | 2706 |  | 66 | Parameter 10 | 2 | R/W
0x03 | 2707 |  | 67 | Parameter 11 | 2 | R/W
0x03 | 2708 |  | 68 | Parameter 12 | 2 | R/W
0x03 | 2709 |  | 69 | Parameter 13 | 2 | R/W
0x03 | 2710 | Group 5 | 70 | Parameter 0 | 2 | R/W |  |  | Parameter page number | 5
0x03 | 2711 |  | 71 | Parameter 1 | 2 | R/W |  |  | 0 Point to control time 1 Voltage
0x03 | 2712 |  | 72 | Parameter 2 | 2 | R/W |  |  | Control time 1 To control time 2Voltage
0x03 | 2713 |  | 73 | Parameter 3 | 2 | R/W |  |  | Voltage from control time 2 to control time 3
0x03 | 2714 |  | 74 | Parameter 4 | 2 | R/W |  |  | Voltage from control time 3 to control time 4
0x03 | 2715 |  | 75 | Parameter 5 | 2 | R/W |  |  | Voltage from control time 4 to control time 5
0x03 | 2716 |  | 76 | Parameter 6 | 2 | R/W |  |  | Voltage from control time 5 to control time 6
0x03 | 2717 |  | 77 | Parameter 7 | 2 | R/W |  |  | Voltage from control time 6 to control time 7
0x03 | 2718 |  | 78 | Parameter 8 | 2 | R/W |  |  | Voltage from control time 7 to control time 8
0x03 | 2719 |  | 79 | Parameter 9 | 2 | R/W |  |  | Control the voltage from 8 to 23:59
0x03 | 2720 |  | 80 | Parameter 10 | 2 | R/W
0x03 | 2721 |  | 81 | Parameter 11 | 2 | R/W
0x03 | 2722 |  | 82 | Parameter 12 | 2 | R/W
0x03 | 2723 |  | 83 | Parameter 13 | 2 | R/W
0x03 | 2724 | Group 6 | 84 | Parameter 0 | 2 | R/W |  |  | Parameter page number | 6
0x03 | 2725 |  | 85 | Parameter 1 | 2 | R/W |  |  | Photovoltaic power sales network logo | 5- Enable
0x03 | 2726 |  | 86 | Parameter 2 | 2 | R/W |  |  | Battery sales network logo | 5- Enable
0x03 | 2727 |  | 87 | Parameter 3 | 2 | R/W
0x03 | 2728 |  | 88 | Parameter 4 | 2 | R/W
0x03 | 2729 |  | 89 | Parameter 5 | 2 | R/W
0x03 | 2730 |  | 90 | Parameter 6 | 2 | R/W |  |  | Temperature correction enable | 5- Enable
0x03 | 2731 |  | 91 | Parameter 7 | 2 | R/W |  |  |  |  | Share
0x03 | 2732 |  | 92 | Parameter 8 | 2 | R/W |  |  | Oil engine control word | 0x5- Enable diesel engine charging; 0x50- Power Limit
0x03 | 2733 |  | 93 | Parameter 9 | 2 | R/W |  |  | Grid control word | 0x5- Enable grid charging; 0x50- Power Limit
0x03 | 2734 |  | 94 | Parameter 10 | 2 | R/W |  |  | Time curve enable | 5
0x03 | 2735 |  | 95 | Parameter 11 | 2 | R/W |  |  | Maximum power of the power grid | 1=100W
0x03 | 2736 |  | 96 | Parameter 12 | 2 | R/W |  |  | Maximum engine power | 1=100W
0x03 | 2737 |  | 97 | Parameter 13 | 2 | R/W |  |  | Maximum reverse flow power | 0-200W
0x03 | 2738 | Group 7 | 98 | Parameter 0 | 2 | R/W |  |  | Parameter page number | 7
0x03 | 2739 |  | 99 | Parameter 1 | 2 | R/W
0x03 | 2740 |  | 100 | Parameter 2 | 2 | R/W
0x03 | 2741 |  | 101 | Parameter 3 | 2 | R/W
0x03 | 2742 |  | 102 | Parameter 4 | 2 | R/W
0x03 | 2743 |  | 103 | Parameter 5 | 2 | R/W
0x03 | 2744 |  | 104 | Parameter 6 | 2 | R/W
0x03 | 2745 |  | 105 | Parameter 7 | 2 | R/W
0x03 | 2746 |  | 106 | Parameter 8 | 2 | R/W
0x03 | 2747 |  | 107 | Parameter 9 | 2 | R/W
0x03 | 2748 |  | 108 | Parameter 10 | 2 | R/W
0x03 | 2749 |  | 109 | Parameter 11 | 2 | R/W
0x03 | 2750 |  | 110 | Parameter 12 | 2 | R/W
0x03 | 2751 |  | 111 | Parameter 13 | 2 | R/W
0x03 | 3504 | Group 8 | 0 | Parameter 0 | 2 | R/W |  |  | Parameter page number | 8
0x03 | 3505 |  | 1 | Parameter 1 | 2 | R/W | 0.1 |  | Positive DC bus bias | '-100~100
0x03 | 3506 |  | 2 | Parameter 2 | 2 | R/W | 0.0001 |  | Positive DC bus slope | '-1000~1000
0x03 | 3507 |  | 3 | Parameter 3 | 2 | R/W | 0.1 |  | Negative DC bus bias | '-100~100
0x03 | 3508 |  | 4 | Parameter 4 | 2 | R/W | 0.0001 |  | Negative DC bus slope | '-1000~1000
0x03 | 3509 |  | 5 | Parameter 5 | 2 | R/W | 0.1 |  | Battery voltage bias | '-100~100
0x03 | 3510 |  | 6 | Parameter 6 | 2 | R/W | 0.0001 |  | Battery voltage slope | '-1000~1000
0x03 | 3511 |  | 7 | Parameter 7 | 2 | R/W | 0.1 |  | Photovoltaic 1 voltage bias | '-100~100
0x03 | 3512 |  | 8 | Parameter 8 | 2 | R/W | 0.0001 |  | PV 1 voltage slope | '-1000~1000
0x03 | 3513 |  | 9 | Parameter 9 | 2 | R/W | 0.1 |  | Photovoltaic 1 voltage bias | '-100~100
0x03 | 3514 |  | 10 | Parameter 10 | 2 | R/W | 0.0001 |  | PV 1 voltage slope | '-1000~1000
0x03 | 3515 |  | 11 | Parameter 11 | 2 | R/W | 0.1 |  | Low voltage DC bias | '-100~100
0x03 | 3516 |  | 12 | Parameter 12 | 2 | R/W | 0.0001 |  | Low voltage DC voltage slope | '-1000~1000
0x03 | 3517 |  | 13 | Parameter 13 | 2 | R/W |  |  | reserve
0x03 | 3518 | Group 9 | 14 | Parameter 0 | 2 | R/W |  |  | Parameter page number | 9
0x03 | 3519 |  | 15 | Parameter 1 | 2 | R/W |  |  | Buck DC voltage bias | '-100~100
0x03 | 3520 |  | 16 | Parameter 2 | 2 | R/W |  |  | Buck DC voltage slope | '-1000~1000
0x03 | 3521 |  | 17 | Parameter 3 | 2 | R/W
0x03 | 3522 |  | 18 | Parameter 4 | 2 | R/W
0x03 | 3523 |  | 19 | Parameter 5 | 2 | R/W
0x03 | 3524 |  | 20 | Parameter 6 | 2 | R/W
0x03 | 3525 |  | 21 | Parameter 7 | 2 | R/W
0x03 | 3526 |  | 22 | Parameter 8 | 2 | R/W
0x03 | 3527 |  | 23 | Parameter 9 | 2 | R/W
0x03 | 3528 |  | 24 | Parameter 10 | 2 | R/W
0x03 | 3529 |  | 25 | Parameter 11 | 2 | R/W |  |  | reserve
0x03 | 3530 |  | 26 | Parameter 12 | 2 | R/W |  |  | reserve
0x03 | 3531 |  | 27 | Parameter 13 | 2 | R/W |  |  | reserve
0x03 | 3532 | Group 1 0 | 28 | Parameter 0 | 2 | R/W |  |  | Parameter page number | 10
0x03 | 3533 |  | 29 | Parameter 1 | 2 | R/W |  |  | Battery Current Bias | '-1000~1000
0x03 | 3534 |  | 30 | Parameter 2 | 2 | R/W |  |  | Battery current slope | '-1000~1000
0x03 | 3535 |  | 31 | Parameter 3 | 2 | R/W |  |  | Photovoltaic 1 current bias | '-1000~1000
0x03 | 3536 |  | 32 | Parameter 4 | 2 | R/W |  |  | Photovoltaic 1 current slope | '-1000~1000
0x03 | 3537 |  | 33 | Parameter 5 | 2 | R/W |  |  | Photovoltaic 2 current bias | '-1000~1000
0x03 | 3538 |  | 34 | Parameter 6 | 2 | R/W |  |  | PV2 current slope | '-1000~1000
0x03 | 3539 |  | 35 | Parameter 7 | 2 | R/W
0x03 | 3540 |  | 36 | Parameter 8 | 2 | R/W
0x03 | 3541 |  | 37 | Parameter 9 | 2 | R/W
0x03 | 3542 |  | 38 | Parameter 10 | 2 | R/W
0x03 | 3543 |  | 39 | Parameter 11 | 2 | R/W
0x03 | 3544 |  | 40 | Parameter 12 | 2 | R/W
0x03 | 3545 |  | 41 | Parameter 13 | 2 | R/W |  |  | reserve
0x03 | 3546 | Group 1 1 | 42 | Parameter 0 | 2 | R/W |  |  | Parameter page number | 11
0x03 | 3547 |  | 43 | Parameter 1 | 2 | R/W | 1% |  | Smart Start SOC | '40~100
0x03 | 3548 |  | 44 | Parameter 2 | 2 | R/W | 1% |  | Smart Shutdown SOC | '30~95
0x03 | 3549 |  | 45 | Parameter 3 | 2 | R/W | 0.01V |  | Smart starting voltage | 4900~6000
0x03 | 3550 |  | 46 | Parameter 4 | 2 | R/W | 0.01V |  | Smart shutdown voltage | 4800~5800
0x03 | 3551 |  | 47 | Parameter 5 | 2 | R/W | 1W |  | Smart photovoltaic start power | 100~12000
0x03 | 3552 |  | 48 | Parameter 6 | 2 | R/W | 0.01Hz |  | AC coupling frequency | 5000~5500
0x03 | 3553 |  | 49 | Parameter 7 | 2 | R/W | 1% |  | Photovoltaic start-up SOC | 0~80
0x03 | 3554 |  | 50 | Parameter 8 | 2 | R/W | 1% |  | Photovoltaic shutdown SOC | 10~90
0x03 | 3555 |  | 51 | Parameter 9 | 2 | R/W | 0.1 |  | Bus maximum voltage | 0~4500
0x03 | 3556 |  | 52 | Parameter 10 | 2 | R/W | 0.1 |  | Bus minimum voltage | 0~3700
0x03 | 3557 |  | 53 | Parameter 11 | 2 | R/W | 0.01V |  | Photovoltaic starting voltage | 4000~5600
0x03 | 3558 |  | 54 | Parameter 12 | 2 | R/W | 0.01V |  | Photovoltaic shutdown voltage | 4200~5800
0x03 | 3559 |  | 55 | Parameter 13 | 2 | R/W | 0.1 |  | Fan start temperature | 0`600
0x03 | 3560 | Group 1 2 | 56 | Parameter 0 | 2 | R/W |  |  | Parameter page number | 12
0x03 | 3561 |  | 57 | Parameter 1 | 2 | R/W |  |  | Float charge voltage | 4800 | Lead-acid batteries | bit15 | 3: Shared enable
0x03 | 3562 |  | 58 | Parameter 2 | 2 | R/W |  |  | Equalizing charging voltage | 5100 |  | bit14
0x03 | 3563 |  | 59 | Parameter 3 | 2 | R/W |  |  | Float charge voltage temperature compensation coefficient | 1=0.1mV/ ℃ |  | bit13
0x03 | 3564 |  | 60 | Parameter 4 | 2 | R/W |  |  | Equalizing charging voltage temperature compensation coefficient | 1=0.1mV/ ℃ |  | bit12
0x03 | 3565 |  | 61 | Parameter 5 | 2 | R/W |  |  | Battery internal resistance | 1= 0.1mΩ |  | bit11
0x03 | 3566 |  | 62 | Parameter 6 | 2 | R/W |  |  | shutdown Shutdown voltage |  |  | bit10
0x03 | 3567 |  | 63 | Parameter 7 | 2 | R/W |  |  | Low voltage alarm voltage |  |  | bit9
0x03 | 3568 |  | 64 | Parameter 8 | 2 | R/W |  |  | Restart voltage |  |  | bit8
0x03 | 3569 |  | 65 | Parameter 9 | 2 | R/W |  |  | equalization hours |  |  | bit7
0x03 | 3570 |  | 66 | Parameter 10 | 2 | R/W |  |  | BMS Agreement Number |  | Lithium battery | bit6
0x03 | 3571 |  | 67 | Parameter 11 | 2 | R/W |  |  | shutdown Shutdown SOC |  |  | bit5
0x03 | 3572 |  | 68 | Parameter 12 | 2 | R/W |  |  | Low battery alarm SOC |  |  | bit4
0x03 | 3573 |  | 69 | Parameter 13 | 2 | R/W |  |  | Restart SoC |  |  | bit3
0x03 | 3574 | Group 1 3 | 70 | Parameter 0 | 2 | R/W |  |  | Parameter page number | 13 |  | bit2
0x03 | 3575 |  | 71 | Parameter 1 | 2 | R/W | [5 empty] | bit1
0x03 | 3576 |  | 72 | Parameter 2 | 2 | R/W | [5 empty] | bit0
0x03 | 3577 |  | 73 | Parameter 3 | 2 | R/W
0x03 | 3578 |  | 74 | Parameter 4 | 2 | R/W
0x03 | 3579 |  | 75 | Parameter 5 | 2 | R/W
0x03 | 3580 |  | 76 | Parameter 6 | 2 | R/W
0x03 | 3581 |  | 77 | Parameter 7 | 2 | R/W
0x03 | 3582 |  | 78 | Parameter 8 | 2 | R/W
0x03 | 3583 |  | 79 | Parameter 9 | 2 | R/W
0x03 | 3584 |  | 80 | Parameter 10 | 2 | R/W
0x03 | 3585 |  | 81 | Parameter 11 | 2 | R/W
0x03 | 3586 |  | 82 | Parameter 12 | 2 | R/W
0x03 | 3587 |  | 83 | Parameter 13 | 2 | R/W
0x03 | 3588 | Group 1 4 | 84 | Parameter 0 | 2 | R/W |  |  | Parameter page number | 14
0x03 | 3589 |  | 85 | Parameter 1 | 2 | R/W
0x03 | 3590 |  | 86 | Parameter 2 | 2 | R/W
0x03 | 3591 |  | 87 | Parameter 3 | 2 | R/W
0x03 | 3592 |  | 88 | Parameter 4 | 2 | R/W
0x03 | 3593 |  | 89 | Parameter 5 | 2 | R/W
0x03 | 3594 |  | 90 | Parameter 6 | 2 | R/W
0x03 | 3595 |  | 91 | Parameter 7 | 2 | R/W
0x03 | 3596 |  | 92 | Parameter 8 | 2 | R/W
0x03 | 3597 |  | 93 | Parameter 9 | 2 | R/W
0x03 | 3598 |  | 94 | Parameter 10 | 2 | R/W
0x03 | 3599 |  | 95 | Parameter 11 | 2 | R/W
0x03 | 3600 |  | 96 | Parameter 12 | 2 | R/W
0x03 | 3601 |  | 97 | Parameter 13 | 2 | R/W
0x03 | 3602 | Group 1 5 | 98 | Parameter 0 | 2 | R/W |  |  | Parameter page number | 31
0x03 | 3603 |  | 99 | Parameter 1 | 2 | R/W |  |  | BMS maximum charging current | 0- 3000
0x03 | 3604 |  | 100 | Parameter 2 | 2 | R/W |  |  | BMS maximum discharge current | 0- 3000
0x03 | 3605 |  | 101 | Parameter 3 | 2 | R/W |  |  | BMS charging maximum voltage | 4600-6000
0x03 | 3606 |  | 102 | Parameter 4 | 2 | R/W |  |  | BMS minimum discharge voltage | 4000-5400
0x03 | 3607 |  | 103 | Parameter 5 | 2 | R/W |  |  | BMS SOC | 0-100
0x03 | 3608 |  | 104 | Parameter 6 | 2 | R/W |  |  | BMS Status
0x03 | 3609 |  | 105 | Parameter 7 | 2 | R/W |  |  | BMS Battery voltage
0x03 | 3610 |  | 106 | Parameter 8 | 2 | R/W |  |  | BMS Battery Current
0x03 | 3611 |  | 107 | Parameter 9 | 2 | R/W
0x03 | 3612 |  | 108 | Parameter 10 | 2 | R/W
0x03 | 3613 |  | 109 | Parameter 11 | 2 | R/W
0x03 | 3614 |  | 110 | Parameter 12 | 2 | R/W |  |  |  | 0
0x03 | 3615 |  | 111 | Parameter 13 | 2 | R/W |  |  | K12=156 , K13=189 Online Upgrade | 0

## Historical fault records (hidden)
History
| Order | Register Address | Data Type | What the data means | Read and Write | byte | Unit ratio | Remark
|  | 1198 | short | History Page | Read and Write
| 0x03 | 1199 | short | Total number of records | Read and Write | 2 |  | 0-200
Record 1 | 0x03 | 1200 | short | years | Read-only | 2 |  | The high byte is the year and the low byte is the month
| 0x03 | 1201 | short | Date and time | Read-only | 2 |  | The high byte is the day and the low byte is the time
| 0x03 | 1202 | short | Minutes and seconds | Read-only | 2 |  | The high byte is minutes and the low byte is seconds
| 0x03 | 1203 | short | Documenting Code | Read-only | 2 |  | The high byte of the record code is 0 and the low byte is the record code
Record 2 | 0x03 | 1204 | short | years | Read-only | 2 |  | The high byte is the year and the low byte is the month
| 0x03 | 1205 | short | Date and time | Read-only | 2 |  | The high byte is the day and the low byte is the time
| 0x03 | 1206 | short | Minutes and seconds | Read-only | 2 |  | The high byte is minutes and the low byte is seconds
| 0x03 | 1207 | short | Documenting Code | Read-only | 2 |  | The high byte of the record code is 0 and the low byte is the record code
Record 3 | 0x03 | 1208 | short | years | Read-only | 2 |  | The high byte is the year and the low byte is the month
| 0x03 | 1209 | short | Date and time | Read-only | 2 |  | The high byte is the day and the low byte is the time
| 0x03 | 1210 | short | Minutes and seconds | Read-only | 2 |  | The high byte is minutes and the low byte is seconds
| 0x03 | 1211 | short | Documenting Code | Read-only | 2 |  | The high byte of the record code is 0 and the low byte is the record code
Record 4 | 0x03 | 1212 | short | years | Read-only | 2 |  | The high byte is the year and the low byte is the month
| 0x03 | 1213 | short | Date and time | Read-only | 2 |  | The high byte is the day and the low byte is the time
| 0x03 | 1214 | short | Minutes and seconds | Read-only | 2 |  | The high byte is minutes and the low byte is seconds
| 0x03 | 1215 | short | Documenting Code | Read-only | 2 |  | The high byte of the record code is 0 and the low byte is the record code
Record 5 | 0x03 | 1216 | short | years | Read-only | 2 |  | The high byte is the year and the low byte is the month
| 0x03 | 1217 | short | Date and time | Read-only | 2 |  | The high byte is the day and the low byte is the time
| 0x03 | 1218 | short | Minutes and seconds | Read-only | 2 |  | The high byte is minutes and the low byte is seconds
| 0x03 | 1219 | short | Documenting Code | Read-only | 2 |  | The high byte of the record code is 0 and the low byte is the record code
Record 6 | 0x03 | 1220 | short | years | Read-only | 2 |  | The high byte is the year and the low byte is the month
| 0x03 | 1221 | short | Date and time | Read-only | 2 |  | The high byte is the day and the low byte is the time
| 0x03 | 1222 | short | Minutes and seconds | Read-only | 2 |  | The high byte is minutes and the low byte is seconds
| 0x03 | 1223 | short | Documenting Code | Read-only | 2 |  | The high byte of the record code is 0 and the low byte is the record code
Record 7 | 0x03 | 1224 | short | years | Read-only | 2 |  | The high byte is the year and the low byte is the month
| 0x03 | 1225 | short | Date and time | Read-only | 2 |  | The high byte is the day and the low byte is the time
| 0x03 | 1226 | short | Minutes and seconds | Read-only | 2 |  | The high byte is minutes and the low byte is seconds
| 0x03 | 1227 | short | Documenting Code | Read-only | 2 |  | The high byte of the record code is 3 and the low byte is the record code
Record 8 | 0x03 | 1228 | short | years | Read-only | 2 |  | The high byte is the year and the low byte is the month
| 0x03 | 1229 | short | Date and time | Read-only | 2 |  | The high byte is the day and the low byte is the time
| 0x03 | 1230 | short | Minutes and seconds | Read-only | 2 |  | The high byte is minutes and the low byte is seconds
| 0x03 | 1231 | short | Documenting Code | Read-only | 2 |  | The high byte of the record code is 3 and the low byte is the record code
Record 9 | 0x03 | 1232 | short | years | Read-only | 2 |  | The high byte is the year and the low byte is the month
| 0x03 | 1233 | short | Date and time | Read-only | 2 |  | The high byte is the day and the low byte is the time
| 0x03 | 1234 | short | Minutes and seconds | Read-only | 2 |  | The high byte is minutes and the low byte is seconds
| 0x03 | 1235 | short | Documenting Code | Read-only | 2 |  | The high byte of the record code is 4 and the low byte is the record code
Record 10 | 0x03 | 1236 | short | years | Read-only | 2 |  | The high byte is the year and the low byte is the month
| 0x03 | 1237 | short | Date and time | Read-only | 2 |  | The high byte is the day and the low byte is the time
| 0x03 | 1238 | short | Minutes and seconds | Read-only | 2 |  | The high byte is minutes and the low byte is seconds
| 0x03 | 1239 | short | Documenting Code | Read-only | 2 |  | The high byte of the record code is 0 and the low byte is the record code
|  | 1348 | short | Event Log Page | Read and Write
|  | 1349 | short | Total number of event records | Read and Write
Event Log 1 | 0x03 | 1350 | short | years | Read-only | 2 |  | The high byte is the year and the low byte is the month
| 0x03 | 1351 | short | Date and time | Read-only | 2 |  | The high byte is the day and the low byte is the time
| 0x03 | 1352 | short | Minutes and seconds | Read-only | 2 |  | The high byte is minutes and the low byte is seconds
| 0x03 | 1353 | short | Documenting Code | Read-only | 2 |  | The high byte of the record code is the record code low byte is 0
Event Log 2 | 0x03 | 1354 | short | years | Read-only | 2 |  | The high byte is the year and the low byte is the month
| 0x03 | 1355 | short | Date and time | Read-only | 2 |  | The high byte is the day and the low byte is the time
| 0x03 | 1356 | short | Minutes and seconds | Read-only | 2 |  | The high byte is minutes and the low byte is seconds
| 0x03 | 1357 | short | Documenting Code | Read-only | 2 |  | The high byte of the record code is the record code low byte is 0
Event Log 3 | 0x03 | 1358 | short | years | Read-only | 2 |  | The high byte is the year and the low byte is the month
| 0x03 | 1359 | short | Date and time | Read-only | 2 |  | The high byte is the day and the low byte is the time
| 0x03 | 1360 | short | Minutes and seconds | Read-only | 2 |  | The high byte is minutes and the low byte is seconds
| 0x03 | 1361 | short | Documenting Code | Read-only | 2 |  | The high byte of the record code is the record code low byte is 0
Event Log 4 | 0x03 | 1362 | short | years | Read-only | 2 |  | The high byte is the year and the low byte is the month
| 0x03 | 1363 | short | Date and time | Read-only | 2 |  | The high byte is the day and the low byte is the time
| 0x03 | 1364 | short | Minutes and seconds | Read-only | 2 |  | The high byte is minutes and the low byte is seconds
| 0x03 | 1365 | short | Documenting Code | Read-only | 2 |  | The high byte of the record code is the record code low byte is 0
Event Log 5 | 0x03 | 1366 | short | years | Read-only | 2 |  | The high byte is the year and the low byte is the month
| 0x03 | 1367 | short | Date and time | Read-only | 2 |  | The high byte is the day and the low byte is the time
| 0x03 | 1368 | short | Minutes and seconds | Read-only | 2 |  | The high byte is minutes and the low byte is seconds
| 0x03 | 1369 | short | Documenting Code | Read-only | 2 |  | The high byte of the record code is the record code low byte is 0
Event Log 6 | 0x03 | 1370 | short | years | Read-only | 2 |  | The high byte is the year and the low byte is the month
| 0x03 | 1371 | short | Date and time | Read-only | 2 |  | The high byte is the day and the low byte is the time
| 0x03 | 1372 | short | Minutes and seconds | Read-only | 2 |  | The high byte is minutes and the low byte is seconds
| 0x03 | 1373 | short | Documenting Code | Read-only | 2 |  | The high byte of the record code is the record code low byte is 0
Event Log 7 | 0x03 | 1374 | short | years | Read-only | 2 |  | The high byte is the year and the low byte is the month
| 0x03 | 1375 | short | Date and time | Read-only | 2 |  | The high byte is the day and the low byte is the time
| 0x03 | 1376 | short | Minutes and seconds | Read-only | 2 |  | The high byte is minutes and the low byte is seconds
| 0x03 | 1377 | short | Documenting Code | Read-only | 2 |  | The high byte of the record code is the record code low byte is 0
Event Log 8 | 0x03 | 1378 | short | years | Read-only | 2 |  | The high byte is the year and the low byte is the month
| 0x03 | 1379 | short | Date and time | Read-only | 2 |  | The high byte is the day and the low byte is the time
| 0x03 | 1380 | short | Minutes and seconds | Read-only | 2 |  | The high byte is minutes and the low byte is seconds
| 0x03 | 1381 | short | Documenting Code | Read-only | 2 |  | The high byte of the record code is the record code low byte is 0
Event Log 9 | 0x03 | 1382 | short | years | Read-only | 2 |  | The high byte is the year and the low byte is the month
| 0x03 | 1383 | short | Date and time | Read-only | 2 |  | The high byte is the day and the low byte is the time
| 0x03 | 1384 | short | Minutes and seconds | Read-only | 2 |  | The high byte is minutes and the low byte is seconds
| 0x03 | 1385 | short | Documenting Code | Read-only | 2 |  | The high byte of the record code is the record code low byte is 0
Event Log 10 | 0x03 | 1386 | short | years | Read-only | 2 |  | The high byte is the year and the low byte is the month
| 0x03 | 1387 | short | Date and time | Read-only | 2 |  | The high byte is the day and the low byte is the time
| 0x03 | 1388 | short | Minutes and seconds | Read-only | 2 |  | The high byte is minutes and the low byte is seconds
| 0x03 | 1389 | short | Documenting Code | Read-only | 2 |  | The high byte of the record code is the record code low byte is 0

## Parameter settings
Serial number | Parameter name |  | illustrate / scope | unit |  | Data Types | Current Value | Setting Value
| English | Chinese |  |  |  |  | Register Address | parameter | Register Address | Setup Instructions | Reference interface
1 | [5 empty] | UINT16 |  | K0=1 | 5000 | When setting parameters to be sent K0Fixed to 1 , K1-K10 To be in D Within the range of column calibration, for example, to set the maximum battery voltage to 58.5V ,but K1=5850 ; To set the battery type to Use Bat V but K10=80 (Right now 0x50 To set the maximum battery discharge current to -225.5A ,but K4=-2255
2 | Bat V Max | Maximum battery voltage | 1500~6000 | 0.01 | V | UINT16 | 2642 | K1 | 5001
3 | Bat V Min | Minimum battery voltage | 1000~5500 | 0.01 | V | UINT16 | 2643 | K2 | 5002
4 | Max A Charge | Maximum battery charging current | 0~3000 | 0.1 | A | UINT16 | 2644 | K3 | 5003
5 | Max A DisCha | Maximum battery discharge current | -3000~0 | 0.1 | A | INT16 | 2645 | K4 | 5004
6 | Bat Cap AH | Battery capacity | 10~2000 | 1 | AH | UINT16 | 2646 | K5 | 5005
7 | PV1 V Max | Photovoltaic 1 Maximum voltage | 1600~5000 | 0.1 | V | UINT16 | 2647 | K6 | 5006
8 | PV1 A Max | Photovoltaic 1 Maximum current | 0~2600 | 0.01 | A | UINT16 | 2648 | K7 | 5007
9 | PV2 V Max | Photovoltaic 2 Maximum voltage | 1600~5000 | 0.1 | V | UINT16 | 2649 | K8 | 5008
10 | PV2 A Max | Photovoltaic 2 Maximum current | 0~2600 | 0.01 | A | UINT16 | 2650 | K9 | 5009
11 | Bat Mode | Battery Type | 0x0005 Lithium 0x0000 Use Bat V 0x0050 Use Bat % |  |  | UINT16 | 2652 | K10 | 5010
1 | [5 empty] | UINT16 |  | K0=2 | 5000 | When setting parameters to be sent K0 Fixed to 2 , K1-K15 To be in D Within the range of column calibration, for example, to set the float charge voltage to 58.5V ,but K1=5850 ; To set the temperature correction to enable (check), then K10=5
2 | Float V | Float charge voltage | 4200~6000 | 0.01 | V | UINT16 | 3561 | K1 | 5001
3 | Equ V | Equalizing charging voltage | 4300~6000 | 0.01 | V | UINT16 | 3562 | K2 | 5002
4 | TempCoF | Float charge temperature compensation coefficient, | -100~0 | 0.1 | mV/ ℃ | INT16 | 3563 | K3 | 5003
5 | TempCoE | Equalizing charge temperature compensation coefficient | -100~0 | 0.1 | mV/ ℃ | INT16 | 3564 | K4 | 5004
6 | BatRes | Battery internal resistance | 0~1000 | 0.1 | mΩ | UINT16 | 3565 | K5 | 5005
7 | Shutdown | Inverter shutdown battery voltage | 4 000-5400 | 0.01 | V | UINT16 | 3566 | K6 | 5006
8 | Low Bat | Inverter warning battery voltage | 4 100-5500 | 0.01 | V | UINT16 | 3567 | K7 | 5007
9 | Restart | Inverter restores battery voltage | 4 200-5600 | 0.01 | V | UINT16 | 3568 | K8 | 5008
10 | Equ Hours | Equalizing charge duration | 0 -12000 | 1 | h | UINT16 | 3569 | K9 | 5009
11 | TempCoEn | Temperature correction enable | 5- Enable 0- prohibit |  |  | UINT16 | 2730 | K10 | 5010
12 | LiBatMode | Lithium battery mode | Display Hexadecimal |  |  | UINT16 | 3570 | K11 | 5011
13 | Shutdown | Inverter shutdown battery SOC value | 0-80 | 1 | % | UINT16 | 3571 | K12 | 5012
14 | Low Bat | Inverter alarm battery SOC value | 5-90 | 1 | % | UINT16 | 3572 | K13 | 5013
15 | Restart | Inverter recovery battery SOC value | 10-100 | 1 | % | UINT16 | 3573 | K14 | 5014
16 | Equ Days | Equalizing charging interval time | 10-100 | 1 | day | UINT16 | 10007 | K15 | 5015
1 | [5 empty] | UINT16 |  | K0=3 | 5000 | When setting parameters to be sent K0 Fixed to 3 , K1-K13 To be in D Within the range of column calibration, for example, to set the maximum grid discharge power 12000W ,but K1=12000 ;
2 | Dischg Pmax W | Maximum power of grid discharge | 0-10000 | 1 | W | UINT16 | 2655 | K1 | 5001
3 | Dischg SOCmin -% | Minimum grid discharge SOC | 5-100 | 1 | % | UINT16 | 2656 | K2 | 5002
4 | Chg SOCmax -% | Grid charging maximum SOC | 0-100 | 1 | % | UINT16 | 2657 | K3 | 5003
5 | Dischg Vmin -V | Grid discharge minimum voltage | 3700-6000 | 0.01 | V | UINT16 | 2658 | K4 | 5004
6 | Chg Vmax -V | Maximum voltage for grid charging | 3700-6000 | 0.01 | V | UINT16 | 2659 | K5 | 5005
7 | Chg Imax -A | Maximum charging current of the power grid | 0-2600 | 0.1 | A | UINT16 | 2660 | K6 | 5006
8 | Chg Imax -A | Maximum diesel charging current | 0-2600 | 0.1 | A | UINT16 | 2661 | K7 | 5007
9 | Dischg Pmax W | Maximum discharge power of oil engine | 0-10000 | 1 | W | UINT16 | 2662 | K8 | 5008
10 | Dischg SOCmin -% | Minimum oil engine discharge SOC | 10-100 | 1 | % | UINT16 | 2663 | K9 | 5009
11 | Chg SOCmax -% | Maximum oil charging SOC | 0-100 | 1 | % | UINT16 | 2664 | K10 | 5010
12 | Dischg Vmin -V | Minimum discharge voltage of oil engine | 3700-6000 | 0.01 | V | UINT16 | 2665 | K11 | 5011
13 | Chg Vmax -V | Maximum voltage for diesel engine charging | 3700-6000 | 0.01 | V | UINT16 | 2666 | K12 | 5012
14 | Disable Chg SOCmin-% | The grid prohibits charging at the minimum SOC | 0-100 | 1 | % | UINT16 | 2667 | K13 | 5013
1 | [5 empty] | UINT16 |  | K0=4 | 5000 | Time curve SOC Page Setup: When setting parameters to be sent K0 Fixed to 4 , K1-K20 To be in D Within the range of column calibration, for example, to set the power control time 1 for 4:00 ,but K1=0400 ; To set the time curve to enable (check the box), K18=5
2 | 4:00 | Power control time 1 | 0~2359 |  |  | UINT16 | 2669 | K1 | 5001
3 | 6:00 | Power control time 2 | 0~2359 |  |  | UINT16 | 2670 | K2 | 5002
4 | 10:00 | Power control time 3 | 0~2359 |  |  | UINT16 | 2671 | K3 | 5003
5 | 11:00 | Power control time 4 | 0~2359 |  |  | UINT16 | 2672 | K4 | 5004
6 | 14:00 | Power control time 5 | 0~2359 |  |  | UINT16 | 2673 | K5 | 5005
7 | 16:00 | Power control time 6 | 0~2359 |  |  | UINT16 | 2674 | K6 | 5006
8 | 20:00 | Power control time 7 | 0~2359 |  |  | UINT16 | 2675 | K7 | 5007
9 | 22:00 | Power control time 8 | 0~2359 |  |  | UINT16 | 2676 | K8 | 5008
10 | 50 | 0 Point to control time 1 of SOC | 0-100 | 1 | % | UINT16 | 2697 | K9 | 5009
11 | 50 | Control time 1 To control time 2 of SOC | 0-100 | 1 | % | UINT16 | 2698 | K10 | 5010
12 | 50 | Control time 2 To control time3 of SOC | 0-100 | 1 | % | UINT16 | 2699 | K11 | 5011
13 | 50 | Control time 3 To control time 4 of SOC | 0-100 | 1 | % | UINT16 | 2700 | K12 | 5012
14 | 50 | Control time 4 To control time 5 of SOC | 0-100 | 1 | % | UINT16 | 2701 | K13 | 5013
15 | 50 | Control time 5 To control time 6 of SOC | 0-100 | 1 | % | UINT16 | 2702 | K14 | 5014
16 | 50 | Control time 6 To control time 7 of SOC | 0-100 | 1 | % | UINT16 | 2703 | K15 | 5015
17 | 50 | Control time 7 To control time 8 of SOC | 0-100 | 1 | % | UINT16 | 2704 | K16 | 5016
18 | 50 | Control time 8 arrive twenty three : 59 of SOC | 0-100 | 1 | % | UINT16 | 2705 | K17 | 5017
19 | Time of Use | Time curve enable | 5= Enable ,0= Disable |  |  | UINT16 | 2734 | K18 | 5018
20 | GridChg | Grid charging enablement | bit=1 Enable |  |  | UINT16 | 2677 | K19 | 5019
21 | GenChg | Diesel engine charging enable | bit=1 Enable |  |  | UINT16 | 2678 | K20 | 5020
1 | [5 empty] | UINT16 |  | K0=5 | 5000 | Time curve voltage page settings: When setting parameters to be sent K0 Fixed to 5 , K1-K20 To be in D Within the range of column calibration, for example, to set 0 Point to control time 1 The voltage is 50,but K1=5000 ; To set the time curve to enable (check the box), K18=5 ; To enable grid charging, set K19=1
2 | 4:00 | Power control time 1 | 0~2359 |  |  | UINT16 | 2669 | K1 | 5001
3 | 6:00 | Power control time 2 | 0~2359 |  |  | UINT16 | 2670 | K2 | 5002
4 | 10:00 | Power control time 3 | 0~2359 |  |  | UINT16 | 2671 | K3 | 5003
5 | 11:00 | Power control time 4 | 0~2359 |  |  | UINT16 | 2672 | K4 | 5004
6 | 14:00 | Power control time 5 | 0~2359 |  |  | UINT16 | 2673 | K5 | 5005
7 | 16:00 | Power control time 6 | 0~2359 |  |  | UINT16 | 2674 | K6 | 5006
8 | 20:00 | Power control time 7 | 0~2359 |  |  | UINT16 | 2675 | K7 | 5007
9 | 22:00 | Power control time 8 | 0~2359 |  |  | UINT16 | 2676 | K8 | 5008
10 | 50 | 0 Point to control time 1 Voltage | 3700~6000 | 0.01 | V | UINT16 | 2711 | K9 | 5009
11 | 50 | Control time 1 To control time 2 Voltage | 3700~6000 | 0.01 | V | UINT16 | 2712 | K10 | 5010
12 | 50 | Control time 2 To control time 3 Voltage | 3700~6000 | 0.01 | V | UINT16 | 2713 | K11 | 5011
13 | 50 | Control time 3 To control time 4 Voltage | 3700~6000 | 0.01 | V | UINT16 | 2714 | K12 | 5012
14 | 50 | Control time 4 To control time 5 Voltage | 3700~6000 | 0.01 | V | UINT16 | 2715 | K13 | 5013
15 | 50 | Control time 5 To control time 6 Voltage | 3700~6000 | 0.01 | V | UINT16 | 2716 | K14 | 5014
16 | 50 | Control time 6 To control time 7 Voltage | 3700~6000 | 0.01 | V | UINT16 | 2717 | K15 | 5015
17 | 50 | Control time 7 To control time 8 Voltage | 3700~6000 | 0.01 | V | UINT16 | 2718 | K16 | 5016
18 | 50 | Control time 8 arrive twenty three : 59 Voltage | 3700~6000 | 0.01 | V | UINT16 | 2719 | K17 | 5017
19 | Time of Use | Time curve enable | 5= Enable ,0= Disable |  |  | UINT16 | 2734 | K18 | 5018
20 | GridChg | Grid charging enablement | bit0=1 Enable |  |  | UINT16 | 2677 | K19 | 5019
21 | GenChg | Diesel engine charging enable | bit0=1 Enable |  |  | UINT16 | 2678 | K20 | 5020
1 | [5 empty] | UINT16 |  | K0=6 | 5000 | Time curve power page settings: When setting parameters to be sentK0 Fixed to 6 , K1-K20 To be in D Within the range of column calibration, for example, to set 0 Point to control time 1 The power is 12000 ,but K1=12000 ; To set the time curve to enable (check the box), K18=5 ; To enable grid charging, set K19=1
2 | 4:00 | Power control time 1 | 0~2359 |  |  | UINT16 | 2669 | K1 | 5001
3 | 6:00 | Power control time 2 | 0~2359 |  |  | UINT16 | 2670 | K2 | 5002
4 | 10:00 | Power control time 3 | 0~2359 |  |  | UINT16 | 2671 | K3 | 5003
5 | 11:00 | Power control time 4 | 0~2359 |  |  | UINT16 | 2672 | K4 | 5004
6 | 14:00 | Power control time 5 | 0~2359 |  |  | UINT16 | 2673 | K5 | 5005
7 | 16:00 | Power control time 6 | 0~2359 |  |  | UINT16 | 2674 | K6 | 5006
8 | 20:00 | Power control time 7 | 0~2359 |  |  | UINT16 | 2675 | K7 | 5007
9 | 22:00 | Power control time 8 | 0~2359 |  |  | UINT16 | 2676 | K8 | 5008
10 | 12000 | 0 Point to control time 1 Power | 0~+10000 | 1 | W | UINT16 | 2683 | K9 | 5009
11 | 12000 | Control time 1 To control time 2 Power | 0~+10000 | 1 | W | UINT16 | 2684 | K10 | 5010
12 | 12000 | Control time 2 To control time 3 Power | 0~+10000 | 1 | W | UINT16 | 2685 | K11 | 5011
13 | 12000 | Control time 3 To control time 4 Power | 0~+10000 | 1 | W | UINT16 | 2686 | K12 | 5012
14 | 12000 | Control time 4 To control time 5 Power | 0~+10000 | 1 | W | UINT16 | 2687 | K13 | 5013
15 | 12000 | Control time 5 To control time 6 Power | 0~+10000 | 1 | W | UINT16 | 2688 | K14 | 5014
16 | 12000 | Control time 6 To control time 7 Power | 0~+10000 | 1 | W | UINT16 | 2689 | K15 | 5015
17 | 12000 | Control time 7 To control time 8 Power | 0~+10000 | 1 | W | UINT16 | 2690 | K16 | 5016
18 | 12000 | Control time 8 arrive twenty three : 59 Power | 0~+10000 | 1 | W | UINT16 | 2691 | K17 | 5017
19 | Time of Use | Time curve enable | 5= Enable ,0= Disable |  |  | UINT16 | 2734 | K18 | 5018
20 | GridChg | Grid charging enablement | bit=1 Enable |  |  | UINT16 | 2677 | K19 | 5019
21 | GenChg | Diesel engine charging enable | bit=1 Enable |  |  | UINT16 | 2678 | K20 | 5020
1 | [5 empty] | UINT16 |  | K0=7 | 5000 | When setting parameters to be sent K0 Fixed to 7 , K1-K16 To be in D Within the range of column calibration, for example, to set the inverter rated voltage to 230V ,but K1=2300 ; To set the maximum grid frequency to 52Hz , K6=5200 ; To check the grid power limit enable, K12=80( Right now 0x50) If the current value is read, there is already a value K12=5, At this time, set the limit enable to K12=85( Right now 0x55)
2 | INV V Rated | Inverter rated voltage | 2180~2320 | 0.1 | V | UINT16 | 642 | K1 | 5001
3 | Inv Hz Rated | Inverter rated frequency | 4600~5400 | 0.01 | Hz | UINT16 | 643 | K2 | 5002
4 | OnGrid A Max | Maximum grid-connected current | 0~3600 | 0.01 | A | UINT16 | 644 | K3 | 5003
5 | Grid Vol Max | Maximum grid voltage | 1600~2640 | 0.1 | V | UINT16 | 645 | K4 | 5004
6 | Grid Vol Min | Minimum grid voltage | 1600~2640 | 0.1 | V | UINT16 | 646 | K5 | 5005
7 | Grid Hz Max | Maximum grid frequency | 4600~5400 | 0.01 | Hz | UINT16 | 647 | K6 | 5006
8 | Grid Hz Min | Minimum grid frequency | 4600~5400 | 0.01 | Hz | UINT16 | 648 | K7 | 5007
9 | Gen Hz Max | Maximum frequency of oil engine | 4600~5400 | 0.01 | Hz | UINT16 | 649 | K8 | 5008
10 | Gen Hz Min | Minimum frequency of oil engine | 4600~5400 | 0.01 | Hz | UINT16 | 650 | K9 | 5009
11 | Gen Vol Max | Maximum voltage of oil engine | 1600~2640 | 0.1 | V | UINT16 | 652 | K10 | 5010
12 | Gen Vol Min | Minimum voltage of oil generator | 1600~2640 | 0.1 | V | UINT16 | 653 | K11 | 5011
13 | GridLitEn | Grid power limit enable | 0xXX5X- Power limit enable 0xXX0X-Power Limit Prohibit |  |  | UINT16 | 2733 | K12 | 5012
14 | Grid Pmax kW | Maximum power of the power grid | 0-200 | 0.1 | kW | UINT16 | 2735 | K13 | 5013
15 | CT Ratio | External current Hall ratio | 0-1000 | 1 |  | UINT16 | 708 | K14 | 5014
1 | [5 empty] | UINT16 |  | K0=8 | 5000 | When setting parameters to be sent K0 Fixed to 8 , K1-K15 To be in D Within the range of column calibration, for example, if you want to set the oil engine interface type to oil engine, then K1=1 ; To check OnGrid Always On , K2=80( Right now 0x50) If you select Only Bat En , then set the limit enable to K2=85( Right now 0x55)
2 | GenPort Type | Oil engine interface type | 5=Smart load 10=AC Coulpe 0= diesel engine |  |  | UINT16 | 701 | K1 | 5001
3 | OnGrid Always On | Ensure intelligent load power supply enable | 0x5=samrt all on Enable 0x50=Only Bat on Enable 0x55= Both are enabled |  |  | UINT16 | 702 | K2 | 5002
| Only Bat En | Only battery-backed smart load power supply is enabled
4 | Gen Mode | AC Couple Operation Mode | 5=VF model 0=PQmodel |  |  | UINT16 | 705 | K3 | 5003
5 | Gen Pmax kW | External oil engine maximum power setting | 0-200 | 0.1 | KW | UINT16 | 2736 | K4 | 5004
6 | Gen Signal En | Control oil engine signal enable | 0x5=Gen Signal En Enable |  |  | UINT16 | 703 | K5 | 5005
7 | Off Soc % | Smart load start up SOC | 40~100 | 1 | % | UINT16 | 3547 | K6 | 5006
8 | On Soc % | Smart load closure SOC | 30~95 | 1 | % | UINT16 | 3548 | K7 | 5007
9 | Off Vol V | Smart load Starting voltage | 4900~6000 | 0.01 | V | UINT16 | 3549 | K8 | 5008
10 | On Vol V | Smart load Shutdown voltage | 4800~5800 | 0.01 | V | UINT16 | 3550 | K9 | 5009
11 | Start Load | Smart load\Ac Couple Power upper limit | 100~12000 | 1 | W | UINT16 | 3551 | K10 | 5010
12 | CoupleFre Hz | Ac Couple frequency | 5000~5500 | 0.01 | Hz | UINT16 | 3552 | K11 | 5011
13 | Off Soc % | Ac Couple start up SOC | 0~80 | 1 | % | UINT16 | 3553 | K12 | 5012
14 | On Soc % | Ac Couple closure SOC | 10~90 | 1 | % | UINT16 | 3554 | K13 | 5013
15 | Off Vol V | Ac Couple Starting voltage | 4000~5600 | 0.01 | V | UINT16 | 3557 | K14 | 5014
16 | On Vol V | Ac Couple Shutdown voltage | 4200~5800 | 0.01 | V | UINT16 | 3558 | K15 | 5015
1 | [5 empty] | UINT16 |  | K0=9 | 5000 | When setting parameters to be sent K0 Fixed to 9 , K1-K15 To be in D Within the range of column calibration, for example, to set Sell First Operation mode, then K1=1 ; To check Solar Sell ,K5=5
2 | Sell First Zero Ex To GridProt Zero Ex To CT | The power sales priority mode does not output to the grid end mode. The power sales priority mode does not output to the CT end mode. | 1=Sell First 2=Zero Ex To GridProt 3=Zero Ex To CT Other = invalid |  |  | UINT16 | 2083 | K1 | 5001
3 | Max Sell Power W | Maximum power selling | 0-10000 | 1 | W | UINT16 | 700 | K2 | 5002
4 | Solar Sell | Photovoltaic power grid switch | 5- Enable, 0- Disable Other = invalid |  |  | UINT16 | 2084 | K3 | 5003
5 | Solar Sell | Photovoltaic power grid switch | 5- Enable, 0- Disable other = invalid |  |  | UINT16 | 2085 | K4 | 5004
6 | GenChgEn | Diesel engine charging enable | 0x5- Enable diesel engine charging; 0x50- Power Limit |  |  | UINT16 | 2732 | K5 | 5005
7 | GridChgEn | Grid charging enablement | 0x5- Enable grid charging; 0x50- Power Limit |  |  | UINT16 | 2733 | K6 | 5006
8 | Zero Ex Power W | Maximum reverse flow power | 0~200 | 1 | W | UINT16 | 2737 | K7 | 5007
1 | [5 empty] | UINT16 |  | K0=10 | 5000
2 | Parallel Units Total Num | Number of parallel units | 0~4 | 1 | tower | UINT16 | 706 | K1 | 5001
3 | Inv Addr | INV Correspondence address | 0~63 odd number |  |  | UINT16 | 651 | K2 | 5002
1 | [5 empty] | UINT16 |  | K0=11 | 5000 | When setting parameters to be sent K0 Fixed to 11 , K1-K3 To be in DWithin the range of column calibration, for example, if the BMS communication method is CAN, then K1=0 ;
2 | BMS COM | BMS Communication | 0- express CAN 1- express RS485 |  |  | UINT16 | 10032 | K1 | 5001
3 | BMS Addr | BMS Correspondence address | 0-120 |  |  | UINT16 | 10005 | K2 | 5002
4 | BMS Prot | BMS Communication Protocol | 0-Felicity 1-PylonTech 2-Chisage 3-Unipower 4-Renon 5-CFE |  |  | UINT16 | 10004 | K3 | 5003
5 | BATShareEn | Shared battery enable | 5- Enable, 0- Disable other = invalid |  |  | UINT16 | 2086 | K4 | 5004

## Debug Group
Debug Group Data and Status
Order | Register Address | Data Type | What the data means | Number of bytes | R/W | unit | Remark
0x03 | 4500 | Group 3state0 |  |  |  |  | For debugging
0x03 | 4501 | Group 3state1
0x03 | 4502 | Group 3state2
0x03 | 4503 | Group 3state3
0x03 | 4504 | Group 3state4
0x03 | 4505 | Group 3state5
0x03 | 4506 | Group 3 Data 0 |  |  |  |  | For debugging
0x03 | 4507 | Group 3 Data 1
0x03 | 4508 | Group 3 Data 2
0x03 | 4509 | Group 3 Data 3
0x03 | 4510 | Group 3 Data 4
0x03 | 4511 | Group 3 Data 5
0x03 | 4512 | Group 3 Data 6
0x03 | 4513 | Group 3 Data 7
0x03 | 4514 | Group 3 Data 8
0x03 | 4515 | Group 3 Data 9
0x03 | 4516 | Group 3 data 10
0x03 | 4517 | Group 3 Data 11
0x03 | 4518 | Group 3 data 12
0x03 | 4519 | Group 3 data 13
0x03 | 4520 | Group 3 data 14
0x03 | 4521 | Group 3 data 15
0x03 | 4522 | Group 3 data 16
0x03 | 4523 | Group 3 data 17
0x03 | 4524 | Group 3 data 18
0x03 | 4525 | Group 3 data 19
0x03 | 4526 | Group 3 data 20
0x03 | 4527 | Group 3 Data 21
0x03 | 4528 | Group 3 data 22
0x03 | 4529 | Group 3 data 23
0x03 | 4530 | Group 3 data 24
0x03 | 4531 | Group 3 data 25
0x03 | 4532 | Group 3 data 26
0x03 | 4533 | Group 3 data 27
0x03 | 4534 | Group 3 data 28
0x03 | 4535 | Group 3 data 29
0x03 | 4536 | Group 3 data 30
0x03 | 4537 | Group 3 Data 31
BMS commissioning group
0x03 | 3650 | Data0 | Battery voltage |  |  |  | RS485 BMS Debugging
0x03 | 3651 | Data 1 | Battery Current
0x03 | 3652 | Data 2 | SOC
0x03 | 3653 | Data 3 | Maximum charging voltage
0x03 | 3654 | Data 4 | Minimum discharge voltage
0x03 | 3655 | Data 5 | Maximum charging current
0x03 | 3656 | Data 6 | Maximum discharge current
0x03 | 3657 | Data 7 | state
0x03 | 3658 | Data 8
0x03 | 3659 | Data 9
0x03 | 3660 | Data 10 | temperature

## Historical data
History
| Order | Register Address | Data Type | What the data means | Read and Write | byte | Remark
|  | 4998 | short | History Page | Read and Write |  | 0- 100
| 0x03 | 4999 | short | Total number of records | Read and Write | 2 | 0- 10 00
Record 1 | 0x03 | 5000 | short | years | Read-only | 2 | The high byte is the year and the low byte is the month
| 0x03 | 5001 | short | Date and time | Read-only | 2 | The high byte is the day and the low byte is the time
| 0x03 | 5002 | short | Minutes and seconds | Read-only | 2 | The high byte is minutes and the low byte is seconds
| 0x03 | 5003 | short | Documenting Code | Read-only | 2 | The high byte of the record code is 0 and the low byte is the record code
Record 2 | 0x03 | 5004 | short | years | Read-only | 2 | The high byte is the year and the low byte is the month
| 0x03 | 5005 | short | Date and time | Read-only | 2 | The high byte is the day and the low byte is the time
| 0x03 | 5006 | short | Minutes and seconds | Read-only | 2 | The high byte is minutes and the low byte is seconds
| 0x03 | 5007 | short | Documenting Code | Read-only | 2 | The high byte of the record code is 0 and the low byte is the record code
Record 3 | 0x03 | 5008 | short | years | Read-only | 2 | The high byte is the year and the low byte is the month
| 0x03 | 5009 | short | Date and time | Read-only | 2 | The high byte is the day and the low byte is the time
| 0x03 | 5010 | short | Minutes and seconds | Read-only | 2 | The high byte is minutes and the low byte is seconds
| 0x03 | 5011 | short | Documenting Code | Read-only | 2 | The high byte of the record code is 0 and the low byte is the record code
Record 4 | 0x03 | 5012 | short | years | Read-only | 2 | The high byte is the year and the low byte is the month
| 0x03 | 5013 | short | Date and time | Read-only | 2 | The high byte is the day and the low byte is the time
| 0x03 | 5014 | short | Minutes and seconds | Read-only | 2 | The high byte is minutes and the low byte is seconds
| 0x03 | 5015 | short | Documenting Code | Read-only | 2 | The high byte of the record code is 0 and the low byte is the record code
Record 5 | 0x03 | 5016 | short | years | Read-only | 2 | The high byte is the year and the low byte is the month
| 0x03 | 5017 | short | Date and time | Read-only | 2 | The high byte is the day and the low byte is the time
| 0x03 | 5018 | short | Minutes and seconds | Read-only | 2 | The high byte is minutes and the low byte is seconds
| 0x03 | 5019 | short | Documenting Code | Read-only | 2 | The high byte of the record code is 0 and the low byte is the record code
Record 6 | 0x03 | 5020 | short | years | Read-only | 2 | The high byte is the year and the low byte is the month
| 0x03 | 5021 | short | Date and time | Read-only | 2 | The high byte is the day and the low byte is the time
| 0x03 | 5022 | short | Minutes and seconds | Read-only | 2 | The high byte is minutes and the low byte is seconds
| 0x03 | 5023 | short | Documenting Code | Read-only | 2 | The high byte of the record code is 0 and the low byte is the record code
Record 7 | 0x03 | 5024 | short | years | Read-only | 2 | The high byte is the year and the low byte is the month
| 0x03 | 5025 | short | Date and time | Read-only | 2 | The high byte is the day and the low byte is the time
| 0x03 | 5026 | short | Minutes and seconds | Read-only | 2 | The high byte is minutes and the low byte is seconds
| 0x03 | 5027 | short | Documenting Code | Read-only | 2 | The high byte of the record code is 3 and the low byte is the record code
Record 8 | 0x03 | 5028 | short | years | Read-only | 2 | The high byte is the year and the low byte is the month
| 0x03 | 5029 | short | Date and time | Read-only | 2 | The high byte is the day and the low byte is the time
| 0x03 | 5030 | short | Minutes and seconds | Read-only | 2 | The high byte is minutes and the low byte is seconds
| 0x03 | 5031 | short | Documenting Code | Read-only | 2 | The high byte of the record code is 3 and the low byte is the record code
Record 9 | 0x03 | 5032 | short | years | Read-only | 2 | The high byte is the year and the low byte is the month
| 0x03 | 5033 | short | Date and time | Read-only | 2 | The high byte is the day and the low byte is the time
| 0x03 | 5034 | short | Minutes and seconds | Read-only | 2 | The high byte is minutes and the low byte is seconds
| 0x03 | 5035 | short | Documenting Code | Read-only | 2 | The high byte of the record code is 4 and the low byte is the record code
Record 10 | 0x03 | 5036 | short | years | Read-only | 2 | The high byte is the year and the low byte is the month
| 0x03 | 5037 | short | Date and time | Read-only | 2 | The high byte is the day and the low byte is the time
| 0x03 | 5038 | short | Minutes and seconds | Read-only | 2 | The high byte is minutes and the low byte is seconds
| 0x03 | 5039 | short | Documenting Code | Read-only | 2 | The high byte of the record code is 0 and the low byte is the record code

## Fault information table
Register Address | Status word | Bit0~Bit15 | Indicates the information content (1: its status is valid; 0: its status is invalid) |  | coding
|  |  | English | Chinese |  | 2 016 Table 8-1 W0 |  |  | 2017 Table 8-1 W1
2061 | Alarm status word 1 | Bit00 | Insulation_Warning | Insulation impedance too low alarm | W01 | bit15 |  |  | bit15 | BMS communication abnormality
|  | Bit01 | Comm_LCD_Lose_Warning | LCD Communication disconnection alarm between the screen and the control board | W02 | bit14 |  |  | bit14
|  | Bit02 | LVRT_Fault_Warning | Low voltage ride-through fault alarm | W03 | bit13 |  |  | bit13
|  | Bit03 | Fan_Faullt_Warning | Fan failure alarm | W04 | bit12 | Fan failure |  | bit12 | Fan failure
|  | Bit04 | PV 1 low voltage warning | PV 1 voltage alarm | W05 | bit11 | Oil engine frequency abnormality |  | bit11
|  | Bit05 | PV 2 low voltage warning | PV 2 voltage alarm | W06 | bit10 | Abnormal oil engine amplitude |  | bit10 | Photovoltaic 2 overvoltage
|  | Bit06 | Battaey low voltage warning | Battery low voltage warning | W07 | bit9 | Abnormal grid frequency |  | bit9 | Photovoltaic 1 overvoltage
|  | Bit07 | ACgrid low voltage warning | Grid low voltage alarm | W08 | bit8 | Abnormal power grid amplitude |  | bit8 | Battery overvoltage
|  | Bit08 | AC low voltage warning | Oil engine low pressure alarm | W09 | bit7 |  |  | bit7
|  | Bit09 | AC_Volt_Unbalance_Warning | AC three-phase voltage unbalance Fault alarm | W10 | bit6 | Load low voltage |  | bit6
|  | Bit10 | AC_PLL_Warning | AC PLL failed | W11 | bit5 | Phase lock failed |  | bit5
|  | Bit11 | Power_Derate_ Warning | Derating alarm | W12 | bit4 | Temperature resistor not connected |  | bit4 | Temperature resistor not connected
|  | Bit12 | Reseverd | Reserve | W13 | bit3 | The phase sequence of the oil engine is wrong | E | bit3 | Battery SOC is low
|  | Bit13 | Heatsink_ Lo Temp_ Warning | IGBT Radiator temperature low alarm | W14 | bit2 | The grid phase sequence is wrong |  | bit2 | Photovoltaic 2 low voltage
|  | Bit14 | BMS Communication Warning | BMS communication disconnection alarm | W15 | bit1 | Oil engine low pressure |  | bit1 | Photovoltaic 1 low voltage
|  | Bit15 | grid _ voltage _Fault | AC end over-voltage or under-voltage error | W16 | bit0 | Grid low voltage |  | bit0 | Battery low voltage
2062 | Alarm status word 2 | Bit00 | grid _GridPhhaseSeque_Fault | AC grid phase sequence error | W17
|  | Bit01 | AC_Freq_Fault | AC power grid over-frequency or under-frequency error | W18 | 2 019 Table 8-3 F0 |  |  | 2020 Table 8-3 F1
|  | Bit02 | gen _ voltage _Fault | Oil generator AC over-voltage or under-voltage error | W19 | bit15 |  |  | bit15
|  | Bit03 | Gen _GridPhhaseSeque_Fault | The AC phase sequence of the oil generator is wrong | W20 | bit14 |  |  | bit14
|  | Bit04 | GEN _Freq_Fault | Diesel generator and power grid over-frequency or under-frequency error | W21 | bit13 |  |  | bit13
|  | Bit05 | Reseverd | Reserve | W22 | bit12 |  |  | bit12
|  | Bit06 | Load low voltage warning | Load low voltage | W23 | bit11 |  |  | bit11
|  | Bit07 | PV2_VoltHigh_warning | Photovoltaic 2 overvoltage | W24 | bit10 | DC undervoltage |  | bit10 | DC bus undervoltage
|  | Bit08 | PV1_VoltHigh_warning | Photovoltaic 1 overvoltage | W25 | bit9 |  |  | bit9 | Permanent insulation resistance failure
[6 empty] | bit8 |  |  | bit8 | GFCI (RCD) AC leakage current fault
|  | Bit09 | Bat_VoltHigh_warning | Battery overvoltage | W26 | bit7 | IGBT Failure |  | bit7
|  | Bit10 | Reseverd | Battery SOC is low | W27 | bit6 |  |  | bit6
|  | Bit11 | Reseverd | Reserve | W28 | bit5 |  |  | bit5
|  | Bit12 | Reseverd | Reserve | W29 | bit4 | Over temperature |  | bit4 | Over temperature
|  | Bit13 | Reseverd | Reserve | W30 | bit3 | Hardware overcurrent |  | bit3 | DC hardware overcurrent
|  | Bit14 | Reseverd | Reserve | W31 | bit2 | Software overcurrent |  | bit2 | DC software overcurrent
|  | Bit15 | Reseverd | Reserve | W32 | bit1 | DC overvoltage |  | bit1 | DC bus overvoltage
[6 empty] | bit0 | Load overvoltage or undervoltage |  | bit0 | Reverse battery connection
Register Address | Status word | Bit0~Bit15 | Indicates the information content (1: its status is valid; 0: its status is invalid) |  | coding
|  |  | English | Chinese |  |  |  |  | 2 021 Table 8-4 F2
2063 | Fault status word 1 | Bit00 | DC Inversed Failure | Battery polarity reverse connection fault | F01 |  |  |  | bit15
|  | Bit01 | Insulattion_Failure | Permanent insulation resistance failure | F02 |  |  |  | bit14
|  | Bit02 | EEPROM_Read_Failure | Read memory error | F03 |  |  |  | bit13
|  | Bit03 | EEPROM_Write_Failure | Write memory error | F04 |  |  |  | bit12
|  | Bit04 | DC soft start Failure | Battery slow down failed | F05 |  |  |  | bit11
|  | Bit05 | Tz_ Dc_OverCurr_Fault | DC hardware overcurrent | F06 |  |  |  | bit10
|  | Bit06 | DC_OverCurr_Failure | DC software overcurrent fault | F07 |  |  |  | bit9
|  | Bit07 | AuxPowerBoard_Failure | Auxiliary switch power supply failure (auxiliary switch power supply | F08 |  |  |  | bit8
|  | Bit08 | IGBT_Failure | IGBT Fault | F09 |  |  |  | bit7
|  | Bit09 | Reseverd | Reserve | F10 |  |  |  | bit6
|  | Bit10 | AC_Main Contactor_Failure | AC main contactor error | F11 |  |  |  | bit5
|  | Bit11 | AC_Slave Contactor_Failure | AC auxiliary contactor error | F12 |  |  |  | bit4
|  | Bit12 | Tz_Ac_OverCurr_Fault | Hardware AC overcurrent fault | F13 |  |  |  | bit3
|  | Bit13 | AC_OverCurr_Failure | AC software overcurrent fault | F14 |  |  |  | bit2
|  | Bit14 | GFCI_Failure | GFCI (RCD) AC leakage current fault | F15 |  |  |  | bit1 | Photovoltaic 2 reverse connection
|  | Bit15 | Tz_COM_OC_Fault | Three-phase current and overcurrent fault | F16 |  |  |  | bit0 | Photovoltaic 1 reverse connection
2064 | Fault status word 2 | Bit00 | BusUnbalance_Fault | DC bus unbalance fault | F17
|  | Bit01 | Load _ voltage _Fault | Load overvoltage or undervoltage | F18
|  | Bit02 | Reseverd | Reserve | F19
|  | Bit03 | Reseverd | Reserve | F20
|  | Bit04 | Reseverd | Reserve | F21
|  | Bit05 | Reseverd | Reserve | F22
|  | Bit06 | Reseverd | Reserve | F23
|  | Bit07 | Grid_Overload_Fault | Grid current overload | F24
|  | Bit08 | Gen_Overload_Fault | Oil generator AC current overload | F25
|  | Bit09 | DC_VoltHigh_Fault | DC bus voltage is too high fault | F26
|  | Bit10 | DC_VoltLow_Fault | DC bus voltage is too low fault | F27
|  | Bit11 | AC_BackFeed_Fault | AC backflow fault | F28
|  | Bit12 | Heatsink_HiTemp_Fault | IGBT Radiator temperature is too high | F29
|  | Bit13 | PV1 Inversed Failure | PV arc fault | F30
|  | Bit14 | PV1 Inversed Failure | Photovoltaic 1 Reverse connection fault | F31
|  | Bit15 | PV2 Inversed Failure | Photovoltaic 2 Reverse connection fault | F32

## Program Upgrade
register | Signal name | Number of bytes | type | Read and Write | Remark
10000-10003 | Manufacturer | 8 | String | RO | Z WGK
10004 | BMS Communication Protocol BMS Prot | 2 | UINT16 | R | 0-Felicity 1-Pylon 2-Chisage 3-Unipower 4-Renon 5-CFE
10005 | BMS Address | 2 | UINT16 | R | 1-255
10006 | BMS battery PACK quantity | 2 | UINT16 | R | 1~16
10007 | Equ Days | 2 | UINT16 | R | 1-100
10008-10023 | Machine model Model name | 32 | String | RO | PVESS-M08K-SA220-DD48
10024-10031 | Serial number | 16 | String | RO | Z 2012KAK8250001
10032 | BMS communication method | 2 | UINT16 | R | 0- indicates CAN 1- indicates RS485
10033 | WIFI upgrade baud rate | 2 | UINT16 | R | 96-9600 192-19200 1152-15200 Others indicate 115200
10034 | INV Software version | 2 | UINT16 | RO | 0 X1123 means V1.1.2.3
10035 | DCDC Software version | 2 | UINT16 | RO | 0 X1123 means V1.1.2.3
10036 | HIMI software version | 2 | UINT16 | RO | 0 X1123 means V1.1.2.3
10037 | Protocol version | 2 | UINT16 | RO | 0 X1123 means V1.1.2.3
13400-13463 | Online upgrade configuration - file name | 128 | String | R
13480-13482 | Online upgrade configuration - File modification time | 6 | MLB | R | 1 , in the upgrade package file properties “ File modification time ” . 2 , Format: Year / moon / day / hour / point / Second
13483-13485 | Upgrade Data Pack - File modification time | 6 | MLB | R
13486-13487 | Upgrade Data Pack - Large file size | 4 | UINT32 | R | File size
13488 | Upgrade Data Pack - Total Frames | 2 | UINT16 | R
13489 | Upgrade Data Pack - Current frame number | 2 | UINT16 | R
13490-13589 | Upgrade Data Pack -Data Bytes 1-100 | 200 | String | R | 200 Bytes, the last frame is not enough and is padded with zeros.
13590 | Online upgrade status | 2 | UINT16 | RO | 0- Not upgraded; 1- The upgrade package is downloading; 2- Download completed, upgrading; 3- Upgrade successful; 4- Upgrade failed;
13591-13640 | Online upgrade received frame number 1-50 | 2*50 | UINT16 | RO | The number of the received packet, from 1 start
13641 | Online upgrade percentage | 2 | UINT16 | RO | 1%

## Debug Data
Order | Register Address | Data Type | What the data means | Number of bytes | R/W | unit |  | Remark | Table 8-1 W0 |  |  | Table 8-2 W 1
0x03 | 1984 | Group 3 Data 0 | [5 empty] | For debugging | bit15 |  |  | bit15 | BMS communication abnormality
0x03 | 1985 | Group 3 Data 1 | [6 empty] | bit14 |  |  | bit14
0x03 | 1986 | Group 3 Data 2 | [6 empty] | bit13 |  |  | bit13
0x03 | 1987 | Group 3 Data 3 | [6 empty] | bit12 | Fan failure |  | bit12 | Fan failure
0x03 | 1988 | Group 3 Data 4 | [6 empty] | bit11 | Oil engine frequency abnormality |  | bit11
0x03 | 1989 | Group 3 Data 5 | [6 empty] | bit10 | Abnormal oil engine amplitude |  | bit10 | Photovoltaic 2 overvoltage
0x03 | 1990 | Group 3 Data 6 | [6 empty] | bit9 | Abnormal grid frequency |  | bit9 | Photovoltaic 1 overvoltage
0x03 | 1991 | Group 3 Data 7 | [6 empty] | bit8 | Abnormal power grid amplitude |  | bit8 | Battery overvoltage
0x03 | 1992 | Group 3 Data 8 | [6 empty] | bit7 |  |  | bit7
0x03 | 1993 | Group 3 Data 9 | [6 empty] | bit6 | Load low voltage |  | bit6
0x03 | 1994 | Group 3 data 10 | [6 empty] | bit5 | Phase lock failed |  | bit5
0x03 | 1995 | Group 3 Data 11 | [6 empty] | bit4 | Temperature resistor not connected |  | bit4 | Temperature resistor not connected
0x03 | 1996 | Group 3 data 12 | [6 empty] | bit3 | The phase sequence of the oil engine is wrong | E | bit3 | Low battery
0x03 | 1997 | Group 3 data 13 | [6 empty] | bit2 | The grid phase sequence is wrong |  | bit2 | Photovoltaic 2 low voltage
0x03 | 1998 | Group 3 data 14 | [6 empty] | bit1 | Oil engine low pressure |  | bit1 | Photovoltaic 1 low voltage
0x03 | 1999 | Group 3 data 15 | [6 empty] | bit0 | Grid low voltage |  | bit0 | Battery low voltage
0x03 | 2000 | Group 3 data 16
0x03 | 2001 | Group 3 data 17 | [6 empty] | Table 8-3 F0 |  |  | Table 8-4 F 1
0x03 | 2002 | Group 3 data 18 | [6 empty] | bit15 |  |  | bit15
0x03 | 2003 | Group 3 data 19 | [6 empty] | bit14 |  |  | bit14
0x03 | 2004 | Group 3 data 20 | [6 empty] | bit13 |  |  | bit13
0x03 | 2005 | Group 3 Data 21 | [6 empty] | bit12 |  |  | bit12
0x03 | 2006 | Group 3 data 22 | [6 empty] | bit11 |  |  | bit11
0x03 | 2007 | Group 3 data 23 | [6 empty] | bit10 | DC undervoltage |  | bit10 | DC bus undervoltage
0x03 | 2008 | Group 3 data 24 | [6 empty] | bit9 |  |  | bit9 | Insulation resistance is too large
0x03 | 2009 | Group 3 data 25 | [6 empty] | bit8 |  |  | bit8 | Leakage current is too large
0x03 | 2010 | Group 3 data 26 | [6 empty] | bit7 | IGBT Failure |  | bit7
0x03 | 2011 | Group 3 data 27 | [6 empty] | bit6 |  |  | bit6
0x03 | 2012 | Group 3 data 28 | [6 empty] | bit5 |  |  | bit5
0x03 | 2013 | Group 3 data 29 | [6 empty] | bit4 | Over temperature |  | bit4 | Over temperature
0x03 | 2014 | Group 3 data 30 | [6 empty] | bit3 | Hardware overcurrent |  | bit3 | DC hardware overcurrent
0x03 | 2015 | Group 3 Data 31 | [6 empty] | bit2 | Software overcurrent |  | bit2 | DC software overcurrent
0x03 | 2016 | Group 2state0 | Alarm status 0 |  |  |  | Table 8-1 | W0 | bit1 | DC overvoltage |  | bit1 | DC bus overvoltage
0x03 | 2017 | Group 2state1 | Alarm status 1 |  |  |  | Table 8-2 | W1 | bit0 | Load overvoltage or undervoltage |  | bit0 | Reverse battery connection
0x03 | 2018 | Group 2state2
0x03 | 2019 | Group 2state3 | Fault state 0 |  |  |  | Table 8-3 | F0 |  |  |  | Table 8- 5 F2
0x03 | 2020 | Group 2state4 | Fault state 1 |  |  |  | Table 8-4 | F1 |  |  |  | bit15
0x03 | 2021 | Group 2state5 | Fault state 2 |  |  |  | Table 8-5 | F2 |  |  |  | bit14
0x03 | 2022 | Group 3state0 | [5 empty] | For debugging |  |  |  | bit13
0x03 | 2023 | Group 3state1 | [9 empty] | bit12
0x03 | 2024 | Group 3state2 | [9 empty] | bit11
0x03 | 2025 | Group 3state3 | [9 empty] | bit10
0x03 | 2026 | Group 3state4 | [9 empty] | bit9
0x03 | 2027 | Group 3state5 | [9 empty] | bit8
bit7
bit6
bit5
bit4
bit3
bit2
[12 empty] | bit1 | Photovoltaic 2 reverse connection
[12 empty] | bit0 | Photovoltaic 1 reverse connection